SIDAMA ZONE WATER, MINE & ENERGY   DEPARTIMENT

SHOYE DAGEYA COMMUNITY WATER SUPPLY PROJECT

(SIDAMA ZONE, DALLE WOREDA)

Prepared By:  B.T. & T.T. (Water Eng.’s)

DES, 2018

Contents                                                                                                    Page

Executive summery	1

1.	INTRODCTION	2

1.1 General	2

1.2.	Specific information of the project area	3

1.3 PROJECT GOAL AND OBJECTIVE	3

1.3.1 Goal	3

1.3.2 Objectives	3

2.	PHYSICAL CONDITIONS OF THE PROJECT AREA	4

2.1 Location	4

2.2 Accessibility	4

2.3 Topography	4

2.4 Climate, Soil and Vegetation	4

3.	SOCIO ECONOMIC CONDITION	5

3.1 Electric Supply	5

3.2 Telephone service	5

3.3 Existing Water Condition.	5

3.3.1 Project area	5

3.3.2. At the water source	5

4.	WATER DEMAND ANALYSIS	6

4.1 Population projection	6

4.1.1   Design period of the Project	6

4.1.2    Design Population	6

4.2 Water source	7

4.3 Per- capita water demand of the target area	7

4.4 Assumption and peaking factor	7

4.5 Water Demand Analysis	8

4.6 Institutional Water Demand	8

4.7 Unaccounted water Demand	8

4.8 Reservoir capacity determination	8

5.	DESIGN OF DISTRIBUTION NET WORK and HYDRAULIC CALCULATION	10

5.1 Pressure main (from BH to 50m3 reservoir)	10

5.3 Network analysis	10

6.	PUMP and GENERATOR	12

6.1 General	12

6.2. Pump capacity and power requirement	12

Therefore from the above table we can conclude that:-	13

6.5	CONCLUSION AND RECOMMENDATION	14

7.	BILL OF QUANTITIES	15

# Executive summery

This design report is describe on Shoye Dageya water supply and sanitation project, which consists Construction of pressure line, Construction of distribution Line, water points, Construction of Anchor Blocks for Pipe Support, Network valve chamber, valve chambers for reservoir, Construction of wet well and Construction of 50m3 reservoirs. The overall cost of this project is 13,396,844.69 Eth.Birr.

# INTRODCTION

## 1.1 General

The need for pure drinking water increases almost in all parts of the region. This is due to population growth, change in lively hood of target group, and others. On the other hand lack of sufficient water source and its quality, scarce investment capital and poor management condition of the scheme make the problem more serious. Therefore water supply activities require high investment capital, needs skilled man power and appropriate management system. To make the scheme sustainable and effective, supportive activities like committee establishment and appropriate, clear management strategy is obligatory for a better result.

Accesses to pure water are a serious problem manifested in all woredas of Sidama zone. Shebedino Woreda is found in Sidam Zone and with poor water supply coverage.

Sidama Zone Water Mine and Energy department with stalk holders has made strong effort to alleviate the problem. This document comprises Socio economic condition, existing water supply coverage of Shoye Dageya, Population projection, Demand analysis, supply and installation of pipes and fittings and construction of other civil works. Basic primary data’s were collected from Shebedino woreda Water office. Some of them are not reliable and correction was made from other sources.

## 1.2.	Specific information of the project area

The project area, Shoye and Dageya is one of the kebeles in Dalle woreda. They have cold climatic condition and found at about 20Km away from Leku town.

## 1.3 PROJECT GOAL AND OBJECTIVE

### 1.3.1 Goal

The goal of the project is to provide pure water and then improve the wellbeing and lively hood of the target community.

### 1.3.2 Objectives

The objectives of the proposed project are:-

- To provide safe, pure and adequate water supply,

- Improve the health status of the community by providing safe & adequate drinking water,

- Strengthen the skill & awareness of the communities towards effective and efficient utilization and management of environmental concerns (i.e. water and its sources)

- Contribute to the national development plans, Universal Access Plan (UAP), to potable water supply.

# PHYSICAL CONDITIONS OF THE PROJECT AREA

## 2.1 Location

The project site is located in Sidama Zone, Dale Woreda. The area has got dense green vegetation with exotic and indigenous tree, fruit specious, perennial and annual crops.

## 2.2 Accessibility

The study area is accessible with Asphalt road Hawassa to Dilla, URAP road and some-weather gravel road. It is about 15Km far away from yirgalem town.

## 2.3 Topography

The topography is gentle slope, steep, medium and it varies. The potential expansion areas of the town are even more than the above ranges.

## 2.4 Climate, Soil and Vegetation

Meteorological data is not found as a result of absence of the station, however it has got cold humid climatic condition and the soil is dominantly clay. The type of vegetation found are predominantly exotic and some indigenous and other perennial crops like ‘’Enset”.

# SOCIO ECONOMIC CONDITION

## 3.1 Electric Supply

There is electric power supply at the kebele and around the project site.

## 3.2 Telephone service

The project area is not provided with telephone service. For the mobile telephone network coverage is available at all parts of the Project area.

## 3.3 Existing Water Condition.

### 3.3.1 Project area

The target community supplied with river water and hand pumps fitted with pump. Water scarcity is still prevailing in the area.

### 3.3.2. At the water source

The potential water source is Bore hole located at Shoye Dageya kebele. The BH was designed to serves as a domestic water source and hygienic purpose to the surrounding community.

# WATER DEMAND ANALYSIS

## 4.1 Population projection

### 4.1.1   Design period of the Project

The economic design period of water supply structures depends up on material life, investment cost (first cost), ease of expansion and others. New water supply schemes are made large enough to meet the needs of the growing population for an economically justifiable number of years in the future. Thus, the design period of a water supply scheme should neither be too long that the present population of the target community is over taxed nor should be too small that just after a few years it may require large extensions due to the increased water requirements. So 20 years of design period is selected for this project.

### 4.1.2    Design Population

There are a numbers of methods to be used to forecast the future population to be served by the proposed water supply system. But, it should be judged to select among various methods of forecasting future population. The basic growth rate for domestic water demand calculation is Central Statistical Authority (CSA) is used. Growth rate and population of Targeted area are 3% and 7514 respectively. There for assuming 3% annual growth rate, using geometric increase method, and considering 2010 E.C as a base year population is projected for every five years intervals as:-

Pn = Po (1+r) t

Where: -	 Pn = Future population with in the design period

Po = Existing population

r = Annual percentage growth rate

t = the design period in years

Using the above parameters, future population is projected for every five years intervals up to the design period of project and tabulated as follows.

## 4.2 Water source

The water source is existing BH found at a lower elevation. As the design criteria indicates that the water source capacity needs to be sized for the total water demand including unaccounted for water.

## 4.3 Per- capita water demand of the target area

Per – capita water demand depends on the availability of other water sources in the surrounding area, climatic factor, quality of water, system of water supply, and other. So, per - capita water demand for these kebeles is assumed to be 25lt/capita per

## 4.4 Assumption and peaking factor

The following assumptions are made to design the water supply project.

- Average Water Demand:-

Average water demand is obtained by multiplying the estimated beneficiaries at a specified year horizon with the total corresponding projected per capita water demand.

- Maximum Day Demand

It is a demand higher in one day of a week than in others. This condition shall be taken in to account by the use of a peak day factor of 1.2.

- Peak Hour Demand

This is due to the fact that water demand varies greatly during the day. Thus the distribution system must be designed to cope with the peak demand. The peak hour factor is expressed as a multiple of the annual average daily demand and additionally to the seasonal and peak day factor and it is 1.8.

## 4.5 Water Demand Analysis

The amount of water to be used for domestic water demand varies widely on mode of services, type & availability of water supply. The use of water for domestic purposes may be divided in to various categories as;-

- Drinking

- Cooking

- Washing

- Bath & shower

For these Kebele domestic water demand considers all the above categories and its mode of service is using public fountains (water points). The study report considers the demand is similar during the design period (which is 25lt/day).

## 4.6 Institutional Water Demand

In this project institutional water demand is not considered.

## 4.7 Unaccounted water Demand

All the water to be produced will not be consumed due to the fact that a portion may be lost because of leakages, over flows of reservoir (s), and due to negligence on part of the dwellers. Thus, for this specific project it is considered and estimated unaccounted water demand is to be 15% of the total average daily water demand.

The population projection indicates only domestic water demand but the design needs to comprise all type of water demand including institutional, and unaccounted for use which is 2% and 15% respectively of average water demand and summarized as table below.

## 4.8 Reservoir capacity determination

In order to design the capacity of a reservoir total average daily water demand and other losses to be considered and it is presented in the following table. Since there is no demand pattern for this particular kebele to determine reservoir capacity and it can be determined using the rule of tomb expressed as 1/3 to ½ of the maximum day demand.

| Table 1.2 Population projection and water demand analysis in Dageya Community water Supply project |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Description | Growth rate per year (%) | Year |  |  |  |  |  |
|  |  | 2010 | 2011 | 2016 | 2021 | 2026 | 2031 |
| Population projection | 3 | 3734 | 3846 | 4459 | 5169 | 5992 | 6946 |
| Average per capital demand(l/c/d) |  |  | 25 | 25 | 25 | 25 | 25 |
| Average daily water demand(l/d) |  |  | 96151 | 111465 | 129218 | 149799 | 173658 |
| Maximum day demand(l/s) |  |  | 1.34 | 1.55 | 1.79 | 2.08 | 2.41 |
| Peak hourly demand(l/s) |  |  | 2.40 | 2.79 | 3.23 | 3.74 | 4.34 |
| Reservoir capacity(m^3) |  |  | 32 | 37 | 43 | 50 | 58 |
| Adopted reservoir capacity(m^3) |  |  | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 |
| Table 1.2 Population projection and water demand analysis in Shoye Community water Supply project |  |  |  |  |  |  |  |
| Description | Growth rate per year(%) | Year |  |  |  |  |  |
|  |  | 2010 | 2011 | 2016 | 2021 | 2026 | 2031 |
| Population projection | 3 | 3780 | 3893 | 4514 | 5232 | 6066 | 7032 |
| Average per capital demand(l/c/d) |  |  | 25 | 25 | 25 | 25 | 25 |
| Average daily water demand(l/d) |  |  | 97335 | 112838 | 130810 | 151645 | 175798 |
| Maximum day demand(l/s) |  |  | 1.35 | 1.57 | 1.82 | 2.11 | 2.44 |
| Peak hourly demand(l/s) |  |  | 2.43 | 2.82 | 3.27 | 3.79 | 4.39 |
| Reservoir capacity(m^3) |  |  | 32 | 38 | 44 | 51 | 59 |
| Adopted reservoir capacity(m^3) |  |  | 50.00 | 50.00 | 50.00 | 50.00 | 50.00 |

As aforementioned above the present population of the target community is neither over taxed nor should be too small that just after a few years it may require large extensions due to the increased water requirements. Therefore 50m3 reservoir is required.

# DESIGN OF DISTRIBUTION NET WORK and HYDRAULIC CALCULATION

## 5.1 Pressure main (from BH to 50m3 reservoir)

The pressure main serves to transfer water from the BH.

The economic diameter (D) of the gravity main is:-

D = 0.9x√Q to 1.2x√Q where Q = in m3/sec. and D in m

Therefore 0.09859m to 1.3145m is required

So adopt100mm of pipe size for Q= 12l/sec

## 5.3 Network analysis

The distribution network will be designed on water point demand, economic size of the pipe, and future expansion.

| Dageya Altitude of reservoir 50m3site above mean sea level= 1856m+9 |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IN.pt | St.pt | Pipe L.th | Pipe Dia (mm) | Velocity (m/s) | Discharge (l/sec) | Head loss (m) | Cum. HL | rh | Cum. rH | Free Head | Node Elv. | Location |
| R | J1 | 18 | 75 | 1.30 | 5.73 | 0.412 | 0.41 | -6 | -6 | 5.6 | 1856.0 |  |
| J1 | wp1 | 411 | 38 | 0.72 | 0.82 | 5.744 | 6.16 | -11 | -17 | 10.8 | 1845.0 | Geremo Shale |
| J1 | J2 | 250 | 75 | 1.11 | 4.91 | 4.200 | 4.61 | -3 | -9 | 4.4 | 1853.0 |  |
| J2 | J3 | 170 | 75 | 1.11 | 4.91 | 2.856 | 7.47 | -4 | -13 | 5.5 | 1849.0 |  |
| J3 | J4 | 85 | 75 | 1.11 | 4.91 | 1.428 | 8.90 | -3 | -16 | 7.1 | 1846.0 |  |
| J4 | wp2 | 6 | 38 | 0.72 | 0.82 | 0.084 | 8.98 | -3 | -19 | 10.0 | 1843.0 | Gareno Gacheno |
| J4 | J5 | 256 | 63 | 1.31 | 4.09 | 7.141 | 16.04 | -14 | -30 | 14.0 | 1832.0 |  |
| J5 | J6 | 206 | 63 | 1.31 | 4.09 | 5.747 | 21.78 | -6 | -36 | 14.2 | 1826.0 |  |
| J6 | wp3 | 320 | 38 | 0.72 | 0.82 | 4.472 | 26.26 | -26 | -62 | 35.7 | 1800.0 | Abebe Balanego |
| J6 | J7 | 216 | 63 | 1.05 | 3.27 | 3.856 | 25.64 | 6 | -30 | 4.4 | 1832.0 |  |
| J7 | HP | 50 | 38 | 0.72 | 0.82 | 0.699 | 26.34 | -2 | -32 | 5.7 | 1830.0 |  |
| J7 | St | 45 | 38 | 0.72 | 0.82 | 0.629 | 26.27 | 0 | -30 | 3.7 | 1832.0 |  |
| J7 | J8 | 110 | 63 | 0.53 | 1.64 | 0.491 | 26.13 | -3 | -33 | 6.9 | 1827.0 |  |
| J8 | J9 | 293 | 50 | 0.83 | 1.64 | 4.153 | 30.28 | -9 | -42 | 11.7 | 1823.0 |  |
| J9 | WP4 | 6 | 38 | 0.72 | 0.82 | 0.084 | 30.37 | -4 | -46 | 15.6 | 1823.0 | Tegenu Tegegn |
| J9 | J10 | 143 | 38 | 0.72 | 0.82 | 1.999 | 32.28 | -1 | -43 | 10.7 | 1822.0 |  |
| J10 | J11 | 56 | 38 | 0.72 | 0.82 | 0.783 | 33.07 | 1 | -42 | 8.9 | 1824.0 |  |
| J11 | J12 | 100 | 38 | 0.72 | 0.82 | 1.398 | 34.46 | -6 | -48 | 13.54 | 1816.0 |  |
| J12 | WP5 | 552 | 38 | 0.72 | 0.82 | 7.715 | 42.18 | -41 | -89 | 46.8 | 1783.0 | Kebebush Bayeto |
| Shoye Altitude of reservoir 50m3site above mean sea level= 1812m+9 |  |  |  |  |  |  |  |  |  |  |  |  |
| IN.pt | St.pt | Pipe L.th | Pipe Dia (mm) | Velocity (m/s) | Discharge (l/sec) | Head loss (m) | Cum. HL | rh | Cum. rH | Free Head | Node Elv. | Location |
| RV | Y1 | 380 | 100 | 0.52 | 4.09 | 1.05 | 1.05 | -13 | -13 | 11.9 | 1805.0 |  |
| Y1 | wp1 | 6 | 38 | 0.72 | 0.82 | 0.08 | 1.14 | 0 | -13 | 11.9 | 1805.0 | Near to church |
| Y1 | Y2 | 158 | 75 | 0.74 | 3.27 | 1.18 | 2.23 | -9 | -22 | 19.8 | 1796.0 |  |
| Y2 | Y3 | 303 | 75 | 0.74 | 3.27 | 2.26 | 4.49 | -22 | -44 | 39.5 | 1774.0 |  |
| Y3 | Y4 | 203 | 75 | 0.74 | 3.27 | 1.52 | 6.01 | 4 | -40 | 34.0 | 1778.0 |  |
| Y4 | Y5 | 142 | 75 | 0.74 | 3.27 | 1.06 | 7.07 | -7 | -47 | 39.9 | 1771.0 |  |
| Y5 | WP2 | 12 | 38 | 0.72 | 0.82 | 0.17 | 7.24 | 0 | -47 | 39.8 | 1771.0 | Alemu Hamesso |
| Y5 | Y6 | 409 | 63 | 0.79 | 2.45 | 4.11 | 11.18 | -1 | -48 | 36.8 | 1770.0 |  |
| Y6 | Y7 | 125 | 63 | 0.79 | 2.45 | 1.26 | 12.43 | 11 | -37 | 24.6 | 1781.0 |  |
| Y7 | Y8 | 163 | 63 | 0.79 | 2.45 | 1.64 | 14.07 | 6 | -31 | 16.9 | 1787.0 |  |
| Y8 | Y9 | 182 | 63 | 0.79 | 2.45 | 1.83 | 15.90 | -3 | -34 | 18.1 | 1784.0 |  |
| Y9 | Y10 | 132 | 63 | 0.79 | 2.45 | 1.33 | 17.22 | -5 | -39 | 21.8 | 1779.0 |  |
| Y10 | Y11 | 134 | 63 | 0.79 | 2.45 | 1.35 | 18.57 | -1 | -40 | 21.4 | 1778.0 |  |
| Y11 | Y12 | 515 | 63 | 0.79 | 2.45 | 5.17 | 23.74 | -2 | -42 | 18.3 | 1776.0 |  |
| Y12 | WP3 | 12 | 38 | 1.44 | 1.64 | 0.67 | 24.41 | 0 | -42 | 17.6 | 1776.0 | Sitota Geremew |
| Y12 | Y13 | 56 | 50 | 0.83 | 1.64 | 0.79 | 24.53 | -16 | -58 | 33.5 | 1760.0 |  |
| Y13 | HP | 18 | 38 | 0.72 | 0.82 | 0.25 | 24.79 | -1 | -59 | 34.2 | 1759.0 |  |
| Y13 | Y14 | 687 | 38 | 0.72 | 0.82 | 9.60 | 34.14 | -14 | -72 | 37.9 | 1746.0 |  |
| Y14 | Y15 | 250 | 38 | 0.72 | 0.82 | 3.49 | 37.63 | -7 | -79 | 41.4 | 1739.0 |  |
| Y15 | WP3 | 6 | 38 | 0.72 | 0.82 | 0.08 | 37.71 | 0 | -79 | 41.3 | 1739.0 | Abebe Senbeto |

## PUMP and GENERATOR

# 6.1 General

A pump may be defined as mechanical dives that will cause a fluid to flow or to be discharged at a higher elevation or higher or pressure pump are used in water works for the purpose of lifting raw water from surface sources and well sources.

## 6.2. Pump capacity and power requirement

According to site report of Shoye Dageya, the well can be pumped at discharge rate of 6 l/sec.

Table 5.1 The work done by the pump and generator is calculated as follows. The work done by Pump and Generator Is Calculated as follows.. S.NO; TDH CALCULATION STEPES; DIMENSION; unit. 1; pumping distance; 2839; M. 2; Discharge; 6.00; L/S. 3; ALLOWANCE; 10.00; M. 4; Pump position /Rizing main/; 141.00; M. 5; DELIVERY HEAD(Elevation difference); 79.00; M. 6; RESERVOIR HEIGHT; 9.00; M. 7; HL (IN DELEVERY PIPE ); 64.77; M. 8; VELOCITY IN DELEVERY PIPE; 1.36; M/S. 9; DIAMETER OF DELEVERY PIPE; 75.00; mm. 10; DISCHARGE; 6.00; L/S. 11; MINOR HL; 3.24; M. 12; TDH; 307.01; M. 13; TDH take; 310.00; m. POWER OF SUBMESIBLE PUMP CALCULATION. 1; TDH; 310.00; M. 2; Discharge; 6.00; L/S. 3; efficiency of pump(E); 60.00; %. 4; POWER OF PUMP=TDH*Q; 30.39; Kw. 102*E. Pp take; 35.00; Kw. 43.75; kVA. power supply (power of generator)=pg. 1; power of pump(Pp); 35.00; kw. 2; Pg = 2*Pp; 70.00; KW. 3; Pg take; 70.00; KW. 4; Pg take; 87.50; KVA.

## Therefore from the above table we can conclude that:-

- Submersible Pump capacity=35Kw/45Kva Head (H)=310m &Discharge Q=6l/s

- Power of generator = 70Kw/87KVAwith all accessories.

6.3 Inputs and Output (Possible suggested solutions)

6.3.1 Project Inputs

The project costs 13,396,844.69 Eth.birr.

6.3.2Output (Possible Suggested Solutions)

Construction of higher altitude Reservoir with a capacity of 50m3.

For the purpose of supplying potable water to the community of Garagalo-Remeda1 in the next 20years the following suggested main points and mechanisms are indicated under.

- Pumping station should be supplied with one Generator house

(Standard hollow concert block Generator House should be Constructed),

- Submersible Pump capacity=35Kw/30.00Kva Head (H)=310m &Discharge Q=6l/s

- Power of generator = 70Kw/87KVA with all accessories. All accessories.

- Design of pressure main with length of 2839m with Diameter of 75mm that will lead up to 50m3 concrete reservoirs that will be constructed.

- A total of eight, six faceted water points are proposed to be constructed near by the settlement area and their location is indicated on the lay out drawing.

- The required distribution pipe network and water points should be constructed as per the detail design considerations specifications and drawings.

- The management of this project should be guided and administered under woreda water supply service.

# CONCLUSION AND RECOMMENDATION

Water is a vital resource for economic and social concerns. This influential scarce resource requires intensive investment cost and appropriate management practices. From practical consideration strong management require for the sustainability of schemes.  This target groups suffers with water shortage, so basic change is required on water supply and sanitation.  As it is observed from the above computations the free head through the system is positive and it is technically feasible, and economical.

# BILL OF QUANTITIES

|  |  |  |  |  |  | Sidama Zone Water Mine & Energy Department |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No | Description |  |  |  |  |  | Unit |  |  |  |  |  | Quantity |  |  |  |  |  | Unit Price |  |  |  |  |  |  |  |  | Total price |  |  |  |  |  |  |  |  |
| A | Supply and Installation of Pipes and Fittings |  |  |  |  |  | Ls |  |  |  |  |  | 1 |  |  |  |  |  | 7,514,709.12 |  |  |  |  |  |  |  |  | 7,514,709.12 |  |  |  |  |  |  |  |  |
| B | Construction of 50m3 Concrete Reservoir |  |  |  |  |  | No. |  |  |  |  |  | 2 |  |  |  |  |  | 495,682.15 |  |  |  |  |  |  |  |  | 991,364.30 |  |  |  |  |  |  |  |  |
| C | Construction of Water Points with Six Faucet |  |  |  |  |  | No. |  |  |  |  |  | 9 |  |  |  |  |  | 35,815.00 |  |  |  |  |  |  |  |  | 322,335.00 |  |  |  |  |  |  |  |  |
| D | Construction of Valve Chambers In Net - Work |  |  |  |  |  | No. |  |  |  |  |  | 12 |  |  |  |  |  | 7,466.02 |  |  |  |  |  |  |  |  | 89,592.24 |  |  |  |  |  |  |  |  |
| E | Construction of valve Chambers In Reservior |  |  |  |  |  | No. |  |  |  |  |  | 2 |  |  |  |  |  | 12,548.25 |  |  |  |  |  |  |  |  | 25,096.50 |  |  |  |  |  |  |  |  |
| F | Supply and Installation of Electro-Mechanical Work |  |  |  |  |  | No. |  |  |  |  |  | 1 |  |  |  |  |  | 1,452,860.00 |  |  |  |  |  |  |  |  | 1,452,860.00 |  |  |  |  |  |  |  |  |
| G | Construction of Guard and Generator house |  |  |  |  |  | No. |  |  |  |  |  | 1 |  |  |  |  |  | 260,272.00 |  |  |  |  |  |  |  |  | 260,272.00 |  |  |  |  |  |  |  |  |
| H | Construction of Anchor Blocks for Pipe Support |  |  |  |  |  | No. |  |  |  |  |  | 14 |  |  |  |  |  | 5,675.07 |  |  |  |  |  |  |  |  | 79,451.01 |  |  |  |  |  |  |  |  |
| I | Pipe and fittings for rod crossing |  |  |  |  |  | No. |  |  |  |  |  | 5 |  |  |  |  |  | 182,750.00 |  |  |  |  |  |  |  |  | 913,750.00 |  |  |  |  |  |  |  |  |
|  | Total |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 11,649,430.17 |  |  |  |  |  |  |  |  |
|  | VAT (15%) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1747414.525 |  |  |  |  |  |  |  |  |
|  | Total including VAT (15%) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 13,396,844.69 |  |  |  |  |  |  |  |  |
| Sidama Zone Water Mine & Energy Department. |  |
| Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Bill No : B Supply & installation of Pipe & fittings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  |  |  | Description |  |  |  |  |  |  | Unit |  |  |  |  |  | Quantity |  |  |  |  |  |  |  | Unit Price |  |  |  |  |  |  |  | Total price |  |  |  |
| 1 |  |  |  | Earth Works |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  |  |  | Trench excavation for pipe laying (0.6* 0.8) *10994m |  |  |  |  |  |  | m3 |  |  |  |  |  | 5,277 |  |  |  |  |  |  |  | 40 |  |  |  |  |  |  |  | 211,088.64 |  |  |  |
| 1.2 |  |  |  | Trench excavation for rock formation (0.6* 0.8) *560 m |  |  |  |  |  |  | m3 |  |  |  |  |  | 269 |  |  |  |  |  |  |  | 50 |  |  |  |  |  |  |  | 13,440.00 |  |  |  |
| 1.3 |  |  |  | Back fill over the pipe with selected soil type inspcted by site Engineer |  |  |  |  |  |  | m3 |  |  |  |  |  | 5,546 |  |  |  |  |  |  |  | 30 |  |  |  |  |  |  |  | 166,380.48 |  |  |  |
| 2 |  |  |  | Supply and laying of different size of GI medium class-B pipe (Technical specification fulfilling IS1239 (part 1)or BS1387 or equivalent weight and wall thickness |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 4" |  |  |  |  |  |  | m |  |  |  |  |  | 380 |  |  |  |  |  |  |  | 850 |  |  |  |  |  |  |  | 323,000.00 |  |  |  |
| 2.1 |  |  |  | 3" |  |  |  |  |  |  | m |  |  |  |  |  | 5,137 |  |  |  |  |  |  |  | 750 |  |  |  |  |  |  |  | 3,852,900.00 |  |  |  |
| 2.2 |  |  |  | 21/2" |  |  |  |  |  |  | m |  |  |  |  |  | 2,448 |  |  |  |  |  |  |  | 650 |  |  |  |  |  |  |  | 1,591,200.00 |  |  |  |
| 2.3 |  |  |  | 2" |  |  |  |  |  |  | m |  |  |  |  |  | 349 |  |  |  |  |  |  |  | 560 |  |  |  |  |  |  |  | 195,440.00 |  |  |  |
| 2.4 |  |  |  | 1 ½” |  |  |  |  |  |  | m |  |  |  |  |  | 2,680 |  |  |  |  |  |  |  | 380 |  |  |  |  |  |  |  | 1,018,400.00 |  |  |  |
| 3 |  |  |  | Supply and Install different size fittings European standard/Class-B/ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | a) Union |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 4" |  |  |  |  |  |  | No |  |  |  |  |  | 35 |  |  |  |  |  |  |  | 380 |  |  |  |  |  |  |  | 13,300.00 |  |  |  |
|  |  |  |  | 3" |  |  |  |  |  |  | No |  |  |  |  |  | 35 |  |  |  |  |  |  |  | 380 |  |  |  |  |  |  |  | 13,300.00 |  |  |  |
|  |  |  |  | 21/2" |  |  |  |  |  |  | No |  |  |  |  |  | 20 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 7,000.00 |  |  |  |
|  |  |  |  | 2" |  |  |  |  |  |  | No |  |  |  |  |  | 12 |  |  |  |  |  |  |  | 260 |  |  |  |  |  |  |  | 3,120.00 |  |  |  |
|  |  |  |  | 1 ½” |  |  |  |  |  |  | No |  |  |  |  |  | 29 |  |  |  |  |  |  |  | 200 |  |  |  |  |  |  |  | 5,800.00 |  |  |  |
|  |  |  |  | b) Nipples |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 4" |  |  |  |  |  |  | No |  |  |  |  |  | 70 |  |  |  |  |  |  |  | 250 |  |  |  |  |  |  |  | 17,500.00 |  |  |  |
|  |  |  |  | 3" |  |  |  |  |  |  | No |  |  |  |  |  | 70 |  |  |  |  |  |  |  | 250 |  |  |  |  |  |  |  | 17,500.00 |  |  |  |
|  |  |  |  | 21/2" |  |  |  |  |  |  | No |  |  |  |  |  | 40 |  |  |  |  |  |  |  | 220 |  |  |  |  |  |  |  | 8,800.00 |  |  |  |
|  |  |  |  | 2" |  |  |  |  |  |  | No |  |  |  |  |  | 24 |  |  |  |  |  |  |  | 200 |  |  |  |  |  |  |  | 4,800.00 |  |  |  |
|  |  |  |  | 1 ½” |  |  |  |  |  |  | No |  |  |  |  |  | 58 |  |  |  |  |  |  |  | 150 |  |  |  |  |  |  |  | 8,700.00 |  |  |  |
|  |  |  |  | c) Reducer |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 4"-3" |  |  |  |  |  |  | No |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 300 |  |  |  |  |  |  |  | 300.00 |  |  |  |
|  |  |  |  | 4"-1 1/2 |  |  |  |  |  |  | No |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 340 |  |  |  |  |  |  |  | 340.00 |  |  |  |
|  |  |  |  | 3”-21/2” |  |  |  |  |  |  | No |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 350.00 |  |  |  |
|  |  |  |  | 21/2”-2 ” |  |  |  |  |  |  | No |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 700.00 |  |  |  |
|  |  |  |  | 21/2”-11/2 ” |  |  |  |  |  |  | No |  |  |  |  |  | 3 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 1,050.00 |  |  |  |
|  |  |  |  | 2”-1 1/2” |  |  |  |  |  |  | No |  |  |  |  |  | 4 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 1,400.00 |  |  |  |
|  |  |  |  | d) Tee |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 4" |  |  |  |  |  |  | No |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 3" |  |  |  |  |  |  | No |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 700.00 |  |  |  |
|  |  |  |  | 21/2" |  |  |  |  |  |  | No |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 300 |  |  |  |  |  |  |  | 600.00 |  |  |  |
|  |  |  |  | 2" |  |  |  |  |  |  | No |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 260 |  |  |  |  |  |  |  | 520.00 |  |  |  |
|  |  |  |  | 1 1/2" |  |  |  |  |  |  | No |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 240 |  |  |  |  |  |  |  | 480.00 |  |  |  |
|  |  |  |  | e) Gate Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  | 4" flanged |  |  |  |  |  |  | No |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 3800 |  |  |  |  |  |  |  | 3,800.00 |  |  |  |
|  |  |  |  | 3" flanged |  |  |  |  |  |  | No |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 3,500 |  |  |  |  |  |  |  | 7,000.00 |  |  |  |
|  |  |  |  | 21/2" |  |  |  |  |  |  | No |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 400 |  |  |  |  |  |  |  | 800.00 |  |  |  |
|  |  |  |  | 2" |  |  |  |  |  |  | No |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 700.00 |  |  |  |
|  |  |  |  | 1 ½” |  |  |  |  |  |  | No |  |  |  |  |  | 6 |  |  |  |  |  |  |  | 300 |  |  |  |  |  |  |  | 1,800.00 |  |  |  |
|  |  |  |  | g) Elbow 150 |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |
|  |  |  |  | 3" |  |  |  |  |  |  | No |  |  |  |  |  | 4 |  |  |  |  |  |  |  | 450 |  |  |  |  |  |  |  | 1,800.00 |  |  |  |
|  |  |  |  | 21/2" |  |  |  |  |  |  | No |  |  |  |  |  | 6 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 2,100.00 |  |  |  |
|  |  |  |  | 2" |  |  |  |  |  |  | No |  |  |  |  |  | 6 |  |  |  |  |  |  |  | 350 |  |  |  |  |  |  |  | 2,100.00 |  |  |  |
| 4 |  |  |  | 1 ½” |  |  |  |  |  |  | No |  |  |  |  |  | 12 |  |  |  |  |  |  |  | 250 |  |  |  |  |  |  |  | 3,000.00 |  |  |  |
| 5 |  |  |  | Synthetic Paint |  |  |  |  |  |  | Kg |  |  |  |  |  | 85 |  |  |  |  |  |  |  | 100 |  |  |  |  |  |  |  | 8,500.00 |  |  |  |
|  |  |  |  | Synthetic Fiber |  |  |  |  |  |  | Kg |  |  |  |  |  | 100 |  |  |  |  |  |  |  | 50 |  |  |  |  |  |  |  | 5,000.00 |  |  |  |
|  |  |  |  | Total cost |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 7,514,709.12 |  |  |  |
| Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Location: - Sidama Zone, Dale Woreda |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Title:- Material requirement and cost estimate of 6m elevated 50m3 RC Reservoir |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  |  | Description |  |  |  |  |  |  |  |  | Unit |  |  |  |  |  | Quantity |  |  |  |  |  |  |  | Unit Price |  |  |  |  |  |  |  | Amount |  |  |
| 1 |  |  | Earth work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  |  | Site clearing to an average depth of 20cm to remove the top vegetated soil |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 29.99 |  |  |  |  |  |  |  | 25.00 |  |  |  |  |  |  |  | 749.75 |  |  |
| 1.2 |  |  | Foundation excavation for mat foundation to a depth of 100 cm below ground level |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 27.00 |  |  |  |  |  |  |  | 40.00 |  |  |  |  |  |  |  | 1,080.00 |  |  |
| 1.3 |  |  | Filling and compaction foundation base with selected material for 20cm |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 11.00 |  |  |  |  |  |  |  | 55.00 |  |  |  |  |  |  |  | 605.00 |  |  |
| 1.4 |  |  | Cart away the excavated surplus material to a distance not less than 100m |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 20.00 |  |  |  |  |  |  |  | 45.00 |  |  |  |  |  |  |  | 900.00 |  |  |
| 1.5 |  |  | placing 35cm thick hardcore of basaltic or equivalent material well rolled, compacted and blinded with crushed stone |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 15.00 |  |  |  |  |  |  |  | 120.00 |  |  |  |  |  |  |  | 1,800.00 |  |  |
| 1.6 |  |  | Back fill around a mat foundation with approved selected materials from site in layer of 15cm |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 9.00 |  |  |  |  |  |  |  | 50.00 |  |  |  |  |  |  |  | 450.00 |  |  |
| 2 |  |  | Concrete work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |
| 2.1 |  |  | Casting 10mm thick lean concrete over hard core C-15 mm ratio(minimum cement content of 150kg/m3) |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 4.50 |  |  |  |  |  |  |  | 1,800.00 |  |  |  |  |  |  |  | 8,100.00 |  |  |
| 2.2 |  |  | Casting 20cm thick Base slab in C-25 RC of minimum cement of 360kg/m3 |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 12.00 |  |  |  |  |  |  |  | 3,000.00 |  |  |  |  |  |  |  | 36,000.00 |  |  |
| 2.3 |  |  | Casting 15cm thick Roof cover slab in C-25 RC of minimum cement of 360kg/m3 |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 10.00 |  |  |  |  |  |  |  | 3,000.00 |  |  |  |  |  |  |  | 30,000.00 |  |  |
| 2.4 |  |  | 25cm thick RC wall concrete as per the drawing |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 12.00 |  |  |  |  |  |  |  | 3,000.00 |  |  |  |  |  |  |  | 36,000.00 |  |  |
| 2.5 |  |  | 50cm*50cm thick RC Column to elevate the reservoir as per the drawing |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 9.00 |  |  |  |  |  |  |  | 3,000.00 |  |  |  |  |  |  |  | 27,000.00 |  |  |
| 2.6 |  |  | 25cm*25cm thick RC beam as per the drawing |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 18.72 |  |  |  |  |  |  |  | 3,000.00 |  |  |  |  |  |  |  | 56,160.00 |  |  |
| 2.5 |  |  | Supply cut, bent and fix in position reinforcement bars |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |
|  |  |  | ø=8mm |  |  |  |  |  |  |  |  | kg |  |  |  |  |  | 392.70 |  |  |  |  |  |  |  | 27.00 |  |  |  |  |  |  |  | 10,602.90 |  |  |
|  |  |  | ø=10mm |  |  |  |  |  |  |  |  | kg |  |  |  |  |  | 1,385.00 |  |  |  |  |  |  |  | 25.00 |  |  |  |  |  |  |  | 34,625.00 |  |  |
|  |  |  | ø=12mm |  |  |  |  |  |  |  |  | kg |  |  |  |  |  | 1,453.00 |  |  |  |  |  |  |  | 25.00 |  |  |  |  |  |  |  | 36,325.00 |  |  |
|  |  |  | ø=14mm |  |  |  |  |  |  |  |  | kg |  |  |  |  |  | 3,395.60 |  |  |  |  |  |  |  | 25.00 |  |  |  |  |  |  |  | 84,890.00 |  |  |
| 2.6 |  |  | supply and fix 3/4 Hexagonal mesh wire for hoop stress |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 89.00 |  |  |  |  |  |  |  | 150.00 |  |  |  |  |  |  |  | 13,350.00 |  |  |
| 2.7 |  |  | Form work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | For floor slab |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 30.00 |  |  |  |  |  |  |  | 105.00 |  |  |  |  |  |  |  | 3,150.00 |  |  |
|  |  |  | For top slab |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 32.00 |  |  |  |  |  |  |  | 105.00 |  |  |  |  |  |  |  | 3,360.00 |  |  |
|  |  |  | For wall |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 55.00 |  |  |  |  |  |  |  | 105.00 |  |  |  |  |  |  |  | 5,775.00 |  |  |
|  |  |  | For Column |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 50.00 |  |  |  |  |  |  |  | 105.00 |  |  |  |  |  |  |  | 5,250.00 |  |  |
|  |  |  | For Beam |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 90.00 |  |  |  |  |  |  |  | 105.00 |  |  |  |  |  |  |  | 9,450.00 |  |  |
|  |  |  | Galvanized iron sheet metal water stop |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 88.42 |  |  |  |  |  |  |  | 150.00 |  |  |  |  |  |  |  | 13,263.00 |  |  |
| 3 |  |  | Masonry Work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 3.1 |  |  | Floor finish 30mm thick trawl and smooth finish with 1:3 cement sand mortar screed |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 30.20 |  |  |  |  |  |  |  | 120.00 |  |  |  |  |  |  |  | 3,624.00 |  |  |
| 4 |  |  | Plumbing Works |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |
| 4.1 |  |  | Pipe supply and connecting work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |
|  |  |  | GS pipe Ø= 4" for outlet |  |  |  |  |  |  |  |  | m |  |  |  |  |  | 6 |  |  |  |  |  |  |  | 387.50 |  |  |  |  |  |  |  | 2,325.00 |  |  |
|  |  |  | GS pipe Ø= 4" for over flow |  |  |  |  |  |  |  |  | m |  |  |  |  |  | 9 |  |  |  |  |  |  |  | 387.50 |  |  |  |  |  |  |  | 3,487.50 |  |  |
|  |  |  | GS pipe Ø= 4" drainage |  |  |  |  |  |  |  |  | m |  |  |  |  |  | 6 |  |  |  |  |  |  |  | 450.00 |  |  |  |  |  |  |  | 2,700.00 |  |  |
|  |  |  | GS pipe Ø= 4" inlet |  |  |  |  |  |  |  |  | m |  |  |  |  |  | 9 |  |  |  |  |  |  |  | 450.00 |  |  |  |  |  |  |  | 4,050.00 |  |  |
|  |  |  | Fitting supply and connecting work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |
|  |  |  | 900 elbow Ø=4" |  |  |  |  |  |  |  |  | Pcs |  |  |  |  |  | 4 |  |  |  |  |  |  |  | 400.00 |  |  |  |  |  |  |  | 1,600.00 |  |  |
|  |  |  | Gate valve Ø=4" |  |  |  |  |  |  |  |  | Pcs |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 2,500.00 |  |  |  |  |  |  |  | 5,000.00 |  |  |
|  |  |  | Water meter Ø=4" |  |  |  |  |  |  |  |  | Pcs |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 8,500.00 |  |  |  |  |  |  |  | 8,500.00 |  |  |
|  |  |  | Union Ø=4" |  |  |  |  |  |  |  |  | Pcs |  |  |  |  |  | 6 |  |  |  |  |  |  |  | 450.00 |  |  |  |  |  |  |  | 2,700.00 |  |  |
|  |  |  | Nipples Ø=4" |  |  |  |  |  |  |  |  | Pcs |  |  |  |  |  | 6 |  |  |  |  |  |  |  | 250.00 |  |  |  |  |  |  |  | 1,500.00 |  |  |
|  |  |  | Tee Ø=4" |  |  |  |  |  |  |  |  | Pcs |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 280.00 |  |  |  |  |  |  |  | 280.00 |  |  |
| 4.2 |  |  | Supply and install lockable steel man-hole cover with all fitting hinge & accessories with lock gate |  |  |  |  |  |  |  |  | no |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 1,500.00 |  |  |  |  |  |  |  | 1,500.00 |  |  |
| 4.3 |  |  | Supply and install both external & internal ladder made of class B GI pipe DN 25mm length 3m having extra 1.0m high handle at the top external ladder |  |  |  |  |  |  |  |  | no |  |  |  |  |  | 2 |  |  |  |  |  |  |  | 2,000.00 |  |  |  |  |  |  |  | 4,000.00 |  |  |
| 4.4 |  |  | Supply & fix 25mm thick quality expansion joint made of Bitumen asphalt applied when necessary |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 6 |  |  |  |  |  |  |  | 450.00 |  |  |  |  |  |  |  | 2,700.00 |  |  |
| 4.5 |  |  | Chiseling and plastering the whole inner wall face and exposed face of concrete works with three coats of cement sand mortar of mix 1:3 |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 115 |  |  |  |  |  |  |  | 98.00 |  |  |  |  |  |  |  | 11,270.00 |  |  |
| 4.6 |  |  | Supply and placing tarred paper b/n lean concrete & floor slab |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 31 |  |  |  |  |  |  |  | 180.00 |  |  |  |  |  |  |  | 5,580.00 |  |  |
| 4.7 |  |  | Supply and painting tarred paper with bituminous mastic |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 31.00 |  |  |  |  |  |  |  | 180.00 |  |  |  |  |  |  |  | 5,580.00 |  |  |
| 5 |  |  | Fencing work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |
| 5.1 |  |  | Fencing around the compound (8*8m) with 10cm well seasoned Tid post stand to the height of 2m above ground level with 0.5m deep concrete foundation and bracing diagonals at the corner. The fence shall be constructed with 3mm barbed wire horizontally every 0.1m bellow 1m and 0.2m above 1m with two ways diagonal bracings |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 64 |  |  |  |  |  |  |  | 100.00 |  |  |  |  |  |  |  | 6,400.00 |  |  |
| 5.5 |  |  | supply and fix corrugated iron sheet door of size 2mx1m with tubular post including lock |  |  |  |  |  |  |  |  | ls |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 2,000.00 |  |  |  |  |  |  |  | 2,000.00 |  |  |
| 6 |  |  | Disinfecting and cleaning internal part of the reservoir |  |  |  |  |  |  |  |  | LS |  |  |  |  |  | 1 |  |  |  |  |  |  |  | 2,000.00 |  |  |  |  |  |  |  | 2,000.00 |  |  |
|  |  |  | Total sum for one 6m elevated 50m3 RCC reservoir |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 495,682.15 |  |  |
| Sidama Zone Water Mine & Energy Department. |  |
| Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Title: - Bills of Quantities for water point construction with six faucets |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  | Description |  |  |  |  |  |  |  | Unit |  |  |  |  |  |  | Quantity |  |  |  |  |  | Unit Price |  |  |  |  |  |  | Total price |  |  |  |  |  |  |
| D |  | CONSTRUCTION OF WATER POINTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | WITH SIX FAUCETS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 |  | Earth work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  | Site clearing to an average depth of 20cm to remove the top vegetated soil |  |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 30 |  |  |  |  |  | 25 |  |  |  |  |  |  | 750 |  |  |  |  |  |  |
| 1.2 |  | Excavation for foundation to a depth of 40 cm |  |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 6.4 |  |  |  |  |  | 45 |  |  |  |  |  |  | 288 |  |  |  |  |  |  |
| 1.3 |  | Cart away the excavated surplus material to a distance not less than 100m |  |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 6.4 |  |  |  |  |  | 30 |  |  |  |  |  |  | 192 |  |  |  |  |  |  |
| 1.4 |  | placing 25cm thick hardcore of basaltic or equivalent material well rolled, compacted and blinded with crushed stone |  |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 4 |  |  |  |  |  | 280 |  |  |  |  |  |  | 1120 |  |  |  |  |  |  |
| 2 |  | Masonry work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |
| 2.1 |  | Construction of masonry wall for six faucet water point embedded in 1:3 cement sand mortar mix |  |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 1.4 |  |  |  |  |  | 985 |  |  |  |  |  |  | 1379 |  |  |  |  |  |  |
| 3 |  | Concrete work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |
| 3.1 |  | Casting 50mm thick lean concrete of 1:3:6 mix ratio(minimum cement content of 150kg/m3) |  |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 18 |  |  |  |  |  | 280 |  |  |  |  |  |  | 5040 |  |  |  |  |  |  |
| 3.2 |  | Mass concrete (1:3:6) mix below foundation wall |  |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 3.06 |  |  |  |  |  | 1400 |  |  |  |  |  |  | 4284 |  |  |  |  |  |  |
| 3.3 |  | Construction of water point cap with concrete of 1:2:3 mix ratio as per the design drawing |  |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 0.9 |  |  |  |  |  | 1200 |  |  |  |  |  |  | 1080 |  |  |  |  |  |  |
| 3.4 |  | Smooth and well strutted zigba form work |  |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 19.4 |  |  |  |  |  | 120 |  |  |  |  |  |  | 2328 |  |  |  |  |  |  |
| 4 |  | Plumbing Works |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |
| 4.1 |  | Pipe supply and connecting work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |
| 4.1.1 |  | GS pipe Ø= 11/2" |  |  |  |  |  |  |  | m |  |  |  |  |  |  | 6 |  |  |  |  |  | 250 |  |  |  |  |  |  | 1500 |  |  |  |  |  |  |
| 4.1.2 |  | GS pipe Ø= 1" |  |  |  |  |  |  |  | m |  |  |  |  |  |  | 6 |  |  |  |  |  | 250 |  |  |  |  |  |  | 1500 |  |  |  |  |  |  |
| 4.1.3 |  | GS pipe Ø= 3/4" |  |  |  |  |  |  |  | m |  |  |  |  |  |  | 3 |  |  |  |  |  | 250 |  |  |  |  |  |  | 750 |  |  |  |  |  |  |
| 4.2 |  | Fitting supply and connecting work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |
| 4.2.1 |  | 900 elbow Ø=11/2" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 6 |  |  |  |  |  | 130 |  |  |  |  |  |  | 780 |  |  |  |  |  |  |
| 4.2.2 |  | Gate valve Ø=11/2" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 1 |  |  |  |  |  | 250 |  |  |  |  |  |  | 250 |  |  |  |  |  |  |
| 4.2.3 |  | Water meter Ø=11/2" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 1 |  |  |  |  |  | 1500 |  |  |  |  |  |  | 1500 |  |  |  |  |  |  |
| 4.2.4 |  | Union Ø=11/2" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 1 |  |  |  |  |  | 75 |  |  |  |  |  |  | 75 |  |  |  |  |  |  |
| 4.2.5 |  | Union Ø=1" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 2 |  |  |  |  |  | 75 |  |  |  |  |  |  | 150 |  |  |  |  |  |  |
| 4.2.6 |  | Nipples Ø=11/2" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 6 |  |  |  |  |  | 75 |  |  |  |  |  |  | 450 |  |  |  |  |  |  |
| 4.2.7 |  | Nipples Ø=1" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 4 |  |  |  |  |  | 75 |  |  |  |  |  |  | 300 |  |  |  |  |  |  |
| 4.2.8 |  | Tee Ø=11/2" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 1 |  |  |  |  |  | 120 |  |  |  |  |  |  | 120 |  |  |  |  |  |  |
| 4.2.9 |  | Cross tee Ø=1" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 2 |  |  |  |  |  | 120 |  |  |  |  |  |  | 240 |  |  |  |  |  |  |
| 4.2.10 |  | Reducer Ø= 11/2" - Ø=1" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 2 |  |  |  |  |  | 90 |  |  |  |  |  |  | 180 |  |  |  |  |  |  |
| 4.2.11 |  | Reducer Ø= 1" - Ø=3/4" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 6 |  |  |  |  |  | 56 |  |  |  |  |  |  | 336 |  |  |  |  |  |  |
| 4.2.12 |  | Coupling Ø= 3/4" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 6 |  |  |  |  |  | 56 |  |  |  |  |  |  | 336 |  |  |  |  |  |  |
| 4.2.13 |  | Faucet Ø=3/4" |  |  |  |  |  |  |  | Pcs |  |  |  |  |  |  | 6 |  |  |  |  |  | 90 |  |  |  |  |  |  | 540 |  |  |  |  |  |  |
| 5 |  | Micellnious and Finishing works |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |
| 5.1 |  | Construction of HCB common walled valve chamber for gate valve and water meter. Price includes supply and fixing anit rust painted and lockable metal valve chamber size 1m*1m with angle iron frame and proper installation of fittings and pointing of HCB |  |  |  |  |  |  |  | no. |  |  |  |  |  |  | 1 |  |  |  |  |  | 2500 |  |  |  |  |  |  | 2500 |  |  |  |  |  |  |
| 5.2 |  | 12mm thick plastering of all exposed surface of concrete and masonry wall with cement mortar mix of 1:3 |  |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 20 |  |  |  |  |  | 85 |  |  |  |  |  |  | 1700 |  |  |  |  |  |  |
| 5.3 |  | 5mm pouring of cement screed placing for floor finish of water points |  |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 11.18 |  |  |  |  |  | 150 |  |  |  |  |  |  | 1677 |  |  |  |  |  |  |
| 6 |  | Fencing work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |
| 6.1 |  | Fencing around the compound (6*6m) with 10cm well seasoned Tid post stand to the height of 2m above ground level with 0.5m deep concrete foundation and bracing diagonals at the corner. The fence shall be constructed with 3mm barbed wire horizontally every 0.1m bellow 1m and 0.2m above 1m with two ways diagonal bracings |  |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 36 |  |  |  |  |  | 100 |  |  |  |  |  |  | 3600 |  |  |  |  |  |  |
| 6.2 |  | Supply and fix corrugated iron sheet door of size 2m*1m with tabular post including pad lock |  |  |  |  |  |  |  | ls |  |  |  |  |  |  | 1 |  |  |  |  |  | 870 |  |  |  |  |  |  | 870 |  |  |  |  |  |  |
|  |  | Total for one water point |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 35,815.00 |  |  |  |  |  |  |
| Sidama Zone Water Mine & Energy Department. |  |
| Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Title: - Bills of Quantities for Valve Chambers Construction In Net - Work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  |  | Description |  |  |  |  |  |  | Unit |  |  |  |  |  |  | Quantity |  |  |  |  |  | Unit Price |  |  |  |  |  |  |  | Total price |  |  |  |  |  |
| 1 |  |  | Earth work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  |  | Site clearing to remove the top soil to a depth of 20cm |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 4 |  |  |  |  |  | 25 |  |  |  |  |  |  |  | 100 |  |  |  |  |  |
| 1.2 |  |  | Excavation for foundation to a depth of 30cm |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 0.588 |  |  |  |  |  | 40 |  |  |  |  |  |  |  | 23.52 |  |  |  |  |  |
| 1.3 |  |  | Cart away the excavated surplus material for a distance of 100m |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 2 |  |  |  |  |  | 30 |  |  |  |  |  |  |  | 60 |  |  |  |  |  |
| 1.4 |  |  | 25cm thick hard core filling under the floor slab |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 0.49 |  |  |  |  |  | 2500 |  |  |  |  |  |  |  | 1225 |  |  |  |  |  |
| 2 |  |  | Masonry work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |
| 2.1 |  |  | Construction of 30 cm thick masonry wall embedded with 1:3 mortar |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 1.5 |  |  |  |  |  | 750 |  |  |  |  |  |  |  | 1125 |  |  |  |  |  |
| 2.2 |  |  | Plastering the internal masonry wall |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 6 |  |  |  |  |  | 150 |  |  |  |  |  |  |  | 900 |  |  |  |  |  |
| 2.3 |  |  | Pointing out the exposed part of the masonry wall |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 8 |  |  |  |  |  | 150 |  |  |  |  |  |  |  | 1200 |  |  |  |  |  |
| 3 |  |  | Concrete work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |
| 3.1 |  |  | Mass concrete for floor slab |  |  |  |  |  |  | m3 |  |  |  |  |  |  | 0.45 |  |  |  |  |  | 850 |  |  |  |  |  |  |  | 382.5 |  |  |  |  |  |
| 3.2 |  |  | Supply & Install 700mm*700mm* 3mm thick lockable steel man-hole cover with all fixing hinges & and angle iron frame and all accessories with lockable gate including anti- rust painted |  |  |  |  |  |  | ls |  |  |  |  |  |  | 1 |  |  |  |  |  | 2000 |  |  |  |  |  |  |  | 2000 |  |  |  |  |  |
| 4 |  |  | Form work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |
| 4.1 |  |  | Smooth and well strutted zigba form work |  |  |  |  |  |  | m2 |  |  |  |  |  |  | 1.5 |  |  |  |  |  | 300 |  |  |  |  |  |  |  | 450 |  |  |  |  |  |
|  |  |  | Total for one valve chamber |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 7,466.02 |  |  |  |  |  |
| Sidama Zone Water Mine & Energy Department |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Title:-Constriction of Valve Chamber for Reservoir |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  |  |  | Description |  |  |  | Unit |  |  |  |  |  |  | Quantity |  |  |  |  |  | Unit Price |  |  |  |  |  |  |  | Total price |  |  |  |  |  |  |  |
| 1.1 |  |  |  | Earth work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.2 |  |  |  | Site clearing to remove top soil to a depth of 20cm |  |  |  | M3 |  |  |  |  |  |  | 0.8 |  |  |  |  |  | 25 |  |  |  |  |  |  |  | 20 |  |  |  |  |  |  |  |
| 1.3 |  |  |  | Excavation for base foundation |  |  |  | m3 |  |  |  |  |  |  | 3.25 |  |  |  |  |  | 30 |  |  |  |  |  |  |  | 97.5 |  |  |  |  |  |  |  |
| 1.4 |  |  |  | 25cm thick hardcore filling |  |  |  | m2 |  |  |  |  |  |  | 3.25 |  |  |  |  |  | 500 |  |  |  |  |  |  |  | 1625 |  |  |  |  |  |  |  |
| 1.5 |  |  |  | Cart away excavated materials |  |  |  | m3 |  |  |  |  |  |  | 3.25 |  |  |  |  |  | 45 |  |  |  |  |  |  |  | 146.25 |  |  |  |  |  |  |  |
| 2 |  |  |  | Masonry Work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| 2.1 |  |  |  | Stone masonry wall |  |  |  | m3 |  |  |  |  |  |  | 3.25 |  |  |  |  |  | 850 |  |  |  |  |  |  |  | 2762.5 |  |  |  |  |  |  |  |
| 3 |  |  |  | Concrete work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| 3.1 |  |  |  | 10cm thick mass concrete above hardcore |  |  |  | m3 |  |  |  |  |  |  | 1 |  |  |  |  |  | 1500 |  |  |  |  |  |  |  | 1500 |  |  |  |  |  |  |  |
| 3.2 |  |  |  | 10cm thick RC concrete for roof slab |  |  |  | m3 |  |  |  |  |  |  | 1 |  |  |  |  |  | 1500 |  |  |  |  |  |  |  | 1500 |  |  |  |  |  |  |  |
| 3.3 |  |  |  | RC bar Ø 10mm |  |  |  | kg |  |  |  |  |  |  | 14 |  |  |  |  |  | 60 |  |  |  |  |  |  |  | 840 |  |  |  |  |  |  |  |
| 3.4 |  |  |  | Black wire Ø 1.5mm |  |  |  | kg |  |  |  |  |  |  | 1 |  |  |  |  |  | 60 |  |  |  |  |  |  |  | 60 |  |  |  |  |  |  |  |
| 4 |  |  |  | Form work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| 4.1 |  |  |  | Form work for roof slab |  |  |  | m2 |  |  |  |  |  |  | 3.9 |  |  |  |  |  | 180 |  |  |  |  |  |  |  | 702 |  |  |  |  |  |  |  |
| 4.2 |  |  |  | Plastering & other finishing work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0 |  |  |  |  |  |  |  |
| 4.3 |  |  |  | Plastering internal wall |  |  |  | m2 |  |  |  |  |  |  | 6.8 |  |  |  |  |  | 150 |  |  |  |  |  |  |  | 1020 |  |  |  |  |  |  |  |
| 4.4 |  |  |  | Pointing of external masonry wall |  |  |  | m2 |  |  |  |  |  |  | 8.5 |  |  |  |  |  | 150 |  |  |  |  |  |  |  | 1275 |  |  |  |  |  |  |  |
| 4.5 |  |  |  | Mane hole cover with angle iron frame and sheet metal including pad lock (70cm*70) |  |  |  | ls |  |  |  |  |  |  | 1 |  |  |  |  |  | 1,000 |  |  |  |  |  |  |  | 1000 |  |  |  |  |  |  |  |
|  |  |  |  | Total cost for reservoir VC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 12,548.25 |  |  |  |  |  |  |  |
| Sidama Zone Water Mine & Energy Department |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Title: - Bills of Quantities for Supply and Installation of Electro Mechanical Equipments |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  | Description |  |  |  |  |  |  |  |  |  |  | Unit |  |  |  |  | Quantity |  |  |  |  | Unit Price |  |  |  |  |  |  |  | Total price |  |  |  |  |  |
| G |  | SUPPLY AND INSTALLATION OF ELECTRO |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | MECHANICAL EQUIPMENT |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 |  | Supply and Installation of Submersible Pump |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  | Supply and install submersible pump with capacity of:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Head, H= 261m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Minimum Efficiency, ƞ=60% |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Discharge, Q=5.5 lit/sec |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | with its full autotransformer switch board |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | including the following accessories and specification:- |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Cable length =150m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Cable size= 3*50mm2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Electrode cable length = 300m |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Electrode cable size=2*1.5mm2 with two electrodes |  |  |  |  |  |  |  |  |  |  | set |  |  |  |  | 1 |  |  |  |  | 800,000. |  |  |  |  |  |  |  | 800,000.00 |  |  |  |  |  |
| 2 |  | Supply and Install Diesel Generator |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
| 2.1 |  | Supply and install diesel generator set with all accessories and Specification having engine power capacity, P= 2*pump Power according to given Q(l/s), ƞ and H (m) |  |  |  |  |  |  |  |  |  |  | set |  |  |  |  | 1 |  |  |  |  | 580,000. |  |  |  |  |  |  |  | 580,000.00 |  |  |  |  |  |
| 3 |  | Supply and Install Class - B- GI Pipes and Fittings for Rising Main |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
| 3.1 |  | Supply and install pipes |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
|  |  | ɸ=3" |  |  |  |  |  |  |  |  |  |  | m |  |  |  |  | 100 |  |  |  |  | 510 |  |  |  |  |  |  |  | 51,000.00 |  |  |  |  |  |
| 3.2 |  | Supply and install fittings |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
| 3.2.1 |  | Elbow |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
|  |  | ɸ=3" |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  | 4 |  |  |  |  | 750 |  |  |  |  |  |  |  | 3,000.00 |  |  |  |  |  |
| 3.2.2 |  | Union |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
|  |  | ɸ=3" |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  | 2 |  |  |  |  | 780 |  |  |  |  |  |  |  | 1,560.00 |  |  |  |  |  |
| 3.2.3 |  | Water meter flanged |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
|  |  | ɸ=3" |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  | 1 |  |  |  |  | 6800 |  |  |  |  |  |  |  | 6,800.00 |  |  |  |  |  |
| 3.2.4 |  | Gate valve flanged |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
|  |  | ɸ=3" |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  | 1 |  |  |  |  | 6800 |  |  |  |  |  |  |  | 6,800.00 |  |  |  |  |  |
| 3.2.5 |  | Check valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
|  |  | ɸ=3" |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  | 1 |  |  |  |  | 1500 |  |  |  |  |  |  |  | 1,500.00 |  |  |  |  |  |
| 3.2.6 |  | Nipples |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |  |  |  |  |
|  |  | ɸ=3" |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  | 4 |  |  |  |  | 390 |  |  |  |  |  |  |  | 1,560.00 |  |  |  |  |  |
| 3.2.8 |  | Bolts and nuts |  |  |  |  |  |  |  |  |  |  | no. |  |  |  |  | 8 |  |  |  |  | 80 |  |  |  |  |  |  |  | 640.00 |  |  |  |  |  |
|  |  | Total sum |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 1,452,860.00 |  |  |  |  |  |
| Sidama Zone Water Mine & Energy Department Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Title:-Bills of Quantities for Construction of Generator and Guard House in HCB |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  |  | Description |  |  |  |  |  |  |  |  |  |  | Unit |  |  |  |  |  | Quantity |  |  |  |  |  |  | Unit Price |  |  |  |  |  |  |  | Total price |  |
| 1 |  |  | Earth work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  |  | Site clearing to an averaged depth 0f 20cm to remove top soil and grubbing |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 63 |  |  |  |  |  |  | 35 |  |  |  |  |  |  |  | 2,205.00 |  |
| 1.2 |  |  | Excavation for foundation trench to a depth of not exceeding 100cm below stripped ground level |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 43.9 |  |  |  |  |  |  | 25 |  |  |  |  |  |  |  | 1,097.50 |  |
| 1.3 |  |  | Excavation for hard formation |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 7.8 |  |  |  |  |  |  | 50 |  |  |  |  |  |  |  | 390.00 |  |
| 1.4 |  |  | Back filling around a foundation with good dry filling material from the site |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 13 |  |  |  |  |  |  | 89 |  |  |  |  |  |  |  | 1,157.00 |  |
| 1.5 |  |  | Back filling under a hard core with good and approved selected materials around the site well rammed and compacted in layers not exceeding 20cm |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 13 |  |  |  |  |  |  | 120 |  |  |  |  |  |  |  | 1,560.00 |  |
| 1.6 |  |  | Cart away surplus excavated material to a distance of 100m |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 43.9 |  |  |  |  |  |  | 120 |  |  |  |  |  |  |  | 5,268.00 |  |
| 1.7 |  |  | Placing 25 cm thick basaltic or equivalent stone hard core well rolled and consolidated and blinded with crushed stone |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 10.4 |  |  |  |  |  |  | 550 |  |  |  |  |  |  |  | 5,720.00 |  |
| 2 |  |  | Masonry work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |
| 2.1 |  |  | Construction of 50cm thick basaltic or equivalent masonry foundation wall to a depth of 70cm below stripped ground level blended and joined in cement mortar of mix (1:30 |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 15.6 |  |  |  |  |  |  | 750 |  |  |  |  |  |  |  | 11,700.00 |  |
| 2.2 |  |  | Construction of 50cm thick basaltic or equivalent masonry foundation wall to a height of 35cm above ground level blended and joined in cement mortar of mix (1:3) |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 11 |  |  |  |  |  |  | 850 |  |  |  |  |  |  |  | 9,350.00 |  |
| 2.3 |  |  | Pointing the exposed external wall surface of the foundation wall with cement mortar 1:3 |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 16 |  |  |  |  |  |  | 580 |  |  |  |  |  |  |  | 9,280.00 |  |
| 2.4 |  |  | 100cm wide semi - dressed stone pavement around generator house |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 24 |  |  |  |  |  |  | 250 |  |  |  |  |  |  |  | 6,000.00 |  |
| 2.5 |  |  | Pointing of stone pavement |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 25.2 |  |  |  |  |  |  | 40 |  |  |  |  |  |  |  | 1,008.00 |  |
| 2.6 |  |  | Construction of semi- circular 30cm diameter drainage ditch as per drawing |  |  |  |  |  |  |  |  |  |  | ls |  |  |  |  |  | 1 |  |  |  |  |  |  | 500 |  |  |  |  |  |  |  | 500.00 |  |
| 2.7 |  |  | Plastering all exposed surfaces of column, ground and upper tie beam , window and door lintel |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 25.1 |  |  |  |  |  |  | 80 |  |  |  |  |  |  |  | 2,008.00 |  |
| 3 |  |  | Concrete work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |
| 3.1 |  |  | Placing 50mm thick lean concrete of Grade C-10 with minimum cement content of 150kg/m3 of concrete over the hard core |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 3.91 |  |  |  |  |  |  | 9800 |  |  |  |  |  |  |  | 38,318.00 |  |
| 3.2 |  |  | Casting 15cm thick reinforced concrete for Generator seat (Basement) with Grade C-20 Concrete with minimum cement content of 320kg/m3cost includes supply and installation of Re-bar and proved anchor bolts and form work fixing |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 1.88 |  |  |  |  |  |  | 1,300.00 |  |  |  |  |  |  |  | 2,444.00 |  |
| 3.3 |  |  | Placing 15cm thick mass concrete of Grade C-20 with minimum cement content of 320kg/m3 of concrete over the lean concrete |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 6.96 |  |  |  |  |  |  | 1,300.00 |  |  |  |  |  |  |  | 9,048.00 |  |
| 3.4 |  |  | C-20 reinforced concrete for ground tie beam and machine foundation |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 2.6 |  |  |  |  |  |  | 1,300.00 |  |  |  |  |  |  |  | 3,380.00 |  |
| 3.5 |  |  | C-20 reinforced concrete for upper tie beam and lintel |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 2.7 |  |  |  |  |  |  | 1,250.00 |  |  |  |  |  |  |  | 3,375.00 |  |
| 3.6 |  |  | C-20 reinforced concrete for column |  |  |  |  |  |  |  |  |  |  | m3 |  |  |  |  |  | 1.1 |  |  |  |  |  |  | 1,250.00 |  |  |  |  |  |  |  | 1,375.00 |  |
| 3.7 |  |  | Reinforcement bar as per construction drawing |  |  |  |  |  |  |  |  |  |  | kg |  |  |  |  |  | 291.5 |  |  |  |  |  |  | 250 |  |  |  |  |  |  |  | 72,875.00 |  |
| 3.8 |  |  | Supply, cut, bend and fixing in position sawn wooden form works of equivalent properly erected and strutted with posts and clings having tight joint notto bleed |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 49.9 |  |  |  |  |  |  | 250 |  |  |  |  |  |  |  | 12,475.00 |  |
| 4 |  |  | Wall and roofing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |
| 4.1 |  |  | Wall work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |
| 4.1.1 |  |  | 20cm thick hollow concrete block wall |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 48.8 |  |  |  |  |  |  | 180 |  |  |  |  |  |  |  | 8,784.00 |  |
| 4.1.2 |  |  | 15cm hollow concrete block wall |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 3.4 |  |  |  |  |  |  | 180 |  |  |  |  |  |  |  | 612.00 |  |
| 4.1.3 |  |  | Pointing of internal and external wall surface |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 90 |  |  |  |  |  |  | 120 |  |  |  |  |  |  |  | 10,800.00 |  |
| 4.2 |  |  | Roofing work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |
| 4.2.1 |  |  | Supply and fix a G-32 G.1 corrugated iron sheets with roof nail having washer fixed to purling of smooth round DN 60mm eucalyptus tree fixed on trusses members made of DN 150mm round eucalyptus tree spaced @ 125cm |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 49.5 |  |  |  |  |  |  | 125 |  |  |  |  |  |  |  | 6,187.50 |  |
| 4.2.2 |  |  | Supply and fix 25*250mm facial board to purloins |  |  |  |  |  |  |  |  |  |  | m |  |  |  |  |  | 6.5 |  |  |  |  |  |  | 150 |  |  |  |  |  |  |  | 975.00 |  |
| 5 |  |  | Doors and windows |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |
| 5.1 |  |  | Supply and fix metal frame door double leaf type with cylindrical lock door size 2.0*2.10m |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  |  | 1 |  |  |  |  |  |  | 2,500.00 |  |  |  |  |  |  |  | 2,500.00 |  |
| 5.2 |  |  | Supply and fix metal door size 0.8*2.10m |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  |  | 1 |  |  |  |  |  |  | 1,800.00 |  |  |  |  |  |  |  | 1,800.00 |  |
| 5.3 |  |  | Supply and fix metal window size (1.20*1.00m) |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  |  | 2 |  |  |  |  |  |  | 2,000.00 |  |  |  |  |  |  |  | 4,000.00 |  |
| 5.4 |  |  | Supply and fix metal window size 1.00*1.00m |  |  |  |  |  |  |  |  |  |  | pcs |  |  |  |  |  | 1 |  |  |  |  |  |  | 2,000.00 |  |  |  |  |  |  |  | 2,000.00 |  |
| 5.5 |  |  | Supply and fix mesh wire for insect netting and ventilation as design 75cm high |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 6 |  |  |  |  |  |  | 130 |  |  |  |  |  |  |  | 780.00 |  |
| 6 |  |  | Fencing work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 0.00 |  |
| 6.1 |  |  | Fencing around the compound (10*10m) with 10cm well seasoned Tid post stand to the height of 2m above ground level with 0.5m deep concrete foundation and bracing diagonals at the corner. The fence shall be constructed with 3mm barbed wire horizontally ever |  |  |  |  |  |  |  |  |  |  | m2 |  |  |  |  |  | 132 |  |  |  |  |  |  | 150 |  |  |  |  |  |  |  | 19,800.00 |  |
| 6.2 |  |  | The door shall be corrugated iron sheet 2m*1m including tabular post and pad lock with all accessories |  |  |  |  |  |  |  |  |  |  | ls |  |  |  |  |  | 1 |  |  |  |  |  |  | 1,500 |  |  |  |  |  |  |  | 1,500.00 |  |
|  |  |  | Total sum |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 260,272.00 |  |
| Sidama Zone Water Mine & Energy Department |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TITLE: Bill of Quantities and specification of Anchor blocks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  |  | Description |  |  |  |  |  | Unit |  |  |  |  |  | Quantity |  |  |  |  |  |  |  |  | Unit Price |  |  |  |  |  |  |  | Total price |  |  |  |  |
| 1 |  |  | Earth works |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  |  | 20cm thick site clearing (2m*1.5m) |  |  |  |  |  | m3 |  |  |  |  |  | 3 |  |  |  |  |  |  |  |  | 30 |  |  |  |  |  |  |  | 90 |  |  |  |  |
| 1.2 |  |  | Foundation excavation depth of |  |  |  |  |  | m3 |  |  |  |  |  | 0.4 |  |  |  |  |  |  |  |  | 45 |  |  |  |  |  |  |  | 18 |  |  |  |  |
|  |  |  | 100cm (0.4m*0.5) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.3 |  |  | cart away the excavated material |  |  |  |  |  | m3 |  |  |  |  |  | 0.384 |  |  |  |  |  |  |  |  | 30 |  |  |  |  |  |  |  | 11.52 |  |  |  |  |
| 1.4 |  |  | 20 cm hard core filling |  |  |  |  |  | m2 |  |  |  |  |  | 0.08 |  |  |  |  |  |  |  |  | 250 |  |  |  |  |  |  |  | 20 |  |  |  |  |
| 1.5 |  |  | Filling back the area around the mat foundation after construction |  |  |  |  |  | m3 |  |  |  |  |  | 0.016 |  |  |  |  |  |  |  |  | 320 |  |  |  |  |  |  |  | 5.12 |  |  |  |  |
| 2 |  |  | concrete work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |  |  |
| 2.1 |  |  | Construct anchor block with 1:2:4 concrete the height of anchor blocks depends on the site condition. |  |  |  |  |  | m3 |  |  |  |  |  | 1.8 |  |  |  |  |  |  |  |  | 2,000 |  |  |  |  |  |  |  | 3,600.00 |  |  |  |  |
| 2.2 |  |  | reinforcement for concrete |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |  |  |
|  |  |  | 10 mm dia at 20 cm c/c for mat foundation |  |  |  |  |  | kg |  |  |  |  |  | 1.105 |  |  |  |  |  |  |  |  | 65 |  |  |  |  |  |  |  | 71.825 |  |  |  |  |
|  |  |  | 10mm for column of the Anchor 2 in number |  |  |  |  |  | kg |  |  |  |  |  | 2.652 |  |  |  |  |  |  |  |  | 65 |  |  |  |  |  |  |  | 172.38 |  |  |  |  |
|  |  |  | 6mm stirrup |  |  |  |  |  | kg |  |  |  |  |  | 0.5958 |  |  |  |  |  |  |  |  | 65 |  |  |  |  |  |  |  | 38.727 |  |  |  |  |
|  |  |  | black/tie wire 1.5mm thick |  |  |  |  |  | kg |  |  |  |  |  | 1.5 |  |  |  |  |  |  |  |  | 65 |  |  |  |  |  |  |  | 97.5 |  |  |  |  |
| 3 |  |  | form work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |  |  |
|  |  |  | fix zigba form work to place concrete |  |  |  |  |  | m2 |  |  |  |  |  | 4.2 |  |  |  |  |  |  |  |  | 250 |  |  |  |  |  |  |  | 1050 |  |  |  |  |
| 4 |  |  | Galvanized metal clamp with necessary fixtures used to hold pipes on head of anchor blocks |  |  |  |  |  | pcs |  |  |  |  |  | 1 |  |  |  |  |  |  |  |  | 500 |  |  |  |  |  |  |  | 500 |  |  |  |  |
|  |  |  | Total cost for one Anchor block |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 5,675.07 |  |  |  |  |
| Sidama Zone Water Mine & Energy Department |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Project Name:Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Title:- Material requirement and cost estimate of Pipe and fittings for Road crossing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| It. No |  |  | Description |  |  |  |  |  |  | Unit |  |  |  |  |  | Quantity |  |  |  |  |  | Unit Price |  |  |  |  |  | Total price |  |  |  |  |  |  |  |  |
| 1 |  |  | Earth Work |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 |  |  | excavation for hard formation crossing pipes (0.6* 1.5) * 25m |  |  |  |  |  |  | M3 |  |  |  |  |  | 45 |  |  |  |  |  | 500 |  |  |  |  |  | 22,500.00 |  |  |  |  |  |  |  |  |
| 1.2 |  |  | Back fill over the pipe with selected soil type inspected by site Engineer |  |  |  |  |  |  | M3 |  |  |  |  |  | 45 |  |  |  |  |  | 450 |  |  |  |  |  | 20,250.00 |  |  |  |  |  |  |  |  |
| 2 |  |  | Supply and laying of GI medium class-B pipes for Road crossing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | - |  |  |  |  |  |  |  |  |
| 2.3 |  |  | Φ=6'' |  |  |  |  |  |  | m |  |  |  |  |  | 50 |  |  |  |  |  | 2,800.00 |  |  |  |  |  | 140,000.00 |  |  |  |  |  |  |  |  |
|  |  |  | Total cost |  |  |  |  |  |  | Birr |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 182,750.00 |  |  |  |  |  |  |  |  |

- Drawings

|  |  |  |  | Project Name: Shoye Dageya Water Supply Project |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Elevated RV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  | Elevated RV |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 3''20= |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Dageya kebele |  |  |  |  |  |  |  |
|  |  |  |  | Shoye kebele |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | BH |  |  |  |  |  |  |  |  |  | Legend :- wp= water point ST= school tap HP= health post BH =bore hole Rv50m3Rcc=50m3 reinforced concrete reservoir |  |  |  |  |  |  |  |
|  |  |  |  | NOT SCALED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |