## PUBLIC FOUNT.Take (hidden)
Chezy Water Works Construction Plc
Take off Sheet Format
Project Name: BALLA WATER SUPPLY PROJECT
Specific Site: Male woreda, balla kebele
Sheet No.: Take off Sheet No-1
Bill No :4. Public Fountain
Item No. | Work Description | Sketch | Unit | Measurment |  |  |  | VOL./ AREA /WEIGHT | Remark
|  |  |  | T/π | L/ pcs | W/ Radius | H/ unit wt. /depth
1 | Earth Work
1.1 | Clearing and removal of top soil to an avereage depth of 20cm |  | m2 | [5 empty] | for six PF
1.2 | Bulk excavation for foundation to a depth not exceeding 30cm |  | m3 | [5 empty] | for six PF | 0
1.3 | Cart away surplus excavated material |  | m3 | [5 empty] | for six PF
m3
m3
1.4 | 25cm thick trachitic hard core blinded with crushed aggregate |  | m2 | [5 empty] | for six PF
2 | CONCRETE WORK
2.1 | mass concret for masonary wall fitting c-15 |  | m3 | 2 | 4.6 | 4.6 | 0.12 | 5.0784 | for Two PF
2.2 | concret copping and vc cover and base slab |  | m3 | 2 | 1 | 0.5 | 0.75 | 0.75 | for Two PF
2.3 | Conceret pavment of 5cm thick |  | m3 |  |  |  |  | 1.986 | for Two PF
|  |  | m3 | 2 | 4.6 | 4.6 | 0.05 | 2.116
|  |  | m3 | 2 | 1.3 | 1 | 0.05 | 0.13 | deduct masonary structure place
3 | Masonary Work
3.1 | Stone masonary as per the drawing |  | m3 |  |  |  |  | 2.5
|  |  | m3 | 2 | 1.5 | 1 | 0.5 | 1.5 | 1st step
|  |  | m3 | 2 | 1 | 1 | 0.25 | 0.5 | 2nd step
|  |  | m3 | 2 | 0.5 | 1 | 0.5 | 0.5 | 3rd step
3.2 | Hard-core filling |  | m3 | 2 | 1.5 | 1 | 1 | 3 | for Two PF
4 | PIPES AND ACCESSORIES
4.1 | GI 1 1/2" pipe |  | m | 2 | 6 |  |  | 12 | for Two PF
4.2 | GI 1 " pipe |  | m | 2 | 3 |  |  | 6 | for Two PF
4.3 | Tee dia.1 1/2" |  | No | 2 | 3 |  |  | 6 | for Two PF
4.4 | Cross Tee 1 1/2" |  | No | 2 | 1 |  |  | 2 | for Two PF
4.5 | Cross Tee 1* 1 1/2" |  | No | 2 | 6 |  |  | 12 | for Two PF
4.6 | Elbow 900 1 1/2" |  | No | 2 | 1 |  |  | 2 | for Two PF
4.7 | Union dia.1 1/2" |  | No | 2 | 1 |  |  | 2 | for Two PF
4.8 | Nipples diam.1 1/2" |  | No | 2 | 4 |  |  | 8 | for Two PF
4.9 | Nipples diam.1 " |  | No | 2 | 6 |  |  | 12 | for Two PF
4.1 | Gate valve 1 1/2" |  | No | 6 | 1 |  |  | 6 | for Six PF
4.11 | water meter 1 1/2" |  | No | 6 | 1 |  |  | 6 | for Six PF
4.12 | Dia.1" faucet |  | No | 6 | 4 |  |  | 24 | for Six PF
4.13 | Coupling 1" |  | No | 2 | 6 |  |  | 12 | for Two PF
5 | FENCE WORK
5.1 | Fence work with eucalyptus post 2m above and 0.6m below ground with interval of 1.2m bind with badbed wire with spacing of 30cm and double diagonal,the post should stand on C-15 conceret foundation |  | m2 | 6 | 6 | 10 |  | 360 | for Six PF
5.2 | enterance gate with Construct sheet iron CIS G-32 and 5*7cm zigba frame with padlock |  | no | 6 | 1 |  |  | 6 | for Six PF
| For the Contractor |  |  |  | For the Supervisor
| Name:- Mubarek A. |  |  |  | Name :
| Signature ----------------------------------- |  |  |  | Signature |  | ________________________
| Date -------------------------------------- |  |  |  | Date: |  | ________________________

## CC take (hidden)
Chezy Water Works Construction Plc
Take off Sheet Format
Project Name: BALLA WATER SUPPLY PROJECT
Specific Site: Male woreda, balla kebele
Sheet No.: Take off Sheet No-1
Bill No :5.Collection Chamber
Item No. | Work Description | Sketch | Unit | Measurment |  |  |  | VOL./ AREA /WEIGHT | Remark
|  |  |  | T/π | L/ pcs | W/ Radius | H/ unit wt. /depth
1 | EARTH WORK & EXCAVATION
1.1 | Site Clearing |  | m2
1.2 | Foundation excavation to depth of 1.2mt |  | m3
1.4 | cart away surrples excavated material and deposited to a distance not exceeding 20mt |  | m3
m3
m3
2 | masonary work
2.1 | construction 40cm thick stone masonary with mix 1:3 |  | m3
2.2 | 30cm thick hard core bilined with creshed stone |  | m2
2.3 | 30cm wide stone Pavement |  | m2
3 | Concrete Work
3.1 | 5cm thick lean concret quality c-7 spread uniformly below the masonary foundation |  | m3
3.2 | mass concret on the surface of hard core filling |  | m2
3.3 | 12 cm thick rc roof slab with man hole opining of 50*50cm |  | m3
4 | pointing and plastering
4.1 | plastering of z internal surface of CH with 3cm thick mortar |  | m2
4.2 | pointing and plastering of all the externally exposed face of masonary wall |  | m2
5 | finishing work
| installation of outlet, drainage and over flow 2" Gi pipe with necessary gate valve |  | no
| For the Contractor |  |  |  | For the Supervisor
| Name:- Mubarek A. |  |  |  | Name :
| Signature ----------------------------------- |  |  |  | Signature |  | ________________________
| Date -------------------------------------- |  |  |  | Date: |  | ________________________

## Am Take (hidden)
Chezy Water Works Construction Plc
Take off Sheet Format
Project Name: BALLA WATER SUPPLY PROJECT
Specific Site: Male woreda, balla kebele
Sheet No.: Take off Sheet No-1
Bill No :#: Amendment order Main line
Item No. | Work Description | Sketch | Unit | Measurment |  |  |  | VOL./ AREA /WEIGHT | Remark
|  |  |  | T/π | L/ pcs | W/ Radius | H/ unit wt. /depth
Amendment order
1 | Pipe and Fitting work
1.1 | HDPE pipe and fitting work from pressure break to spring eye
1.1.1 | Excavation of pipe line trench excavation of 30cm *60cm |  | m3 |  | 2290 | 0.3 | 0.6 | 412.2
1.1.2 | backfilling of treanch |  | m3 |  | 2290 | 0.3 | 0.6 | 412.2
1.1.3 | Supply & installation of HDPE pipe PE 100 series dia.2" with OD 58.88mm PN-10 wall thickness 5.8mm |  | mt |  | 2290 |  |  | 2290
1.1.4 | HDPE fitting work
| Female adapter dia.50.8mm |  | Pcs |  | 8 |  |  | 8
| Male adapter dia.50.8mm |  | Pcs |  | 5 |  |  | 5
| Straight commpression coupling 50.8mm*50.8mm |  | Pcs |  | 11 |  |  | 11
| Saddle clamp 50.8*2" |  | Pcs |  | 2 |  |  | 2
| Union 50.8mm |  | Pcs |  | 10 |  |  | 10
| Elbow 90deg 2" |  | Pcs |  | 6 |  |  | 6
| Elbow 45deg 2" |  | Pcs |  | 3 |  |  | 3
| Gs adapter 2" |  | Pcs |  | 2 |  |  | 2
1.2 | GI pipe and fitting work from pressure break to Reservoir
1.2.1 | Excavation of pipe line trench excavation of 60cm *80cm |  | m3 |  | 306 | 0.6 | 0.8 | 146.88
1.2.2 | backfilling of treanch |  | m3 |  | 306 | 0.6 | 0.8 | 146.88
1.2.3 | Supply and Installation of 2" medium class GI pipe |  | Pcs |  | 51 |  |  | 51
GI fitting work
| Gate valve 2" |  | Pcs |  | 1 |  |  | 1
| 2" Union |  | Pcs |  | 2 |  |  | 2
| 2" Nipples |  | Pcs |  | 4 |  |  | 4
| 2" Elbow 90* |  | Pcs |  | 3 |  |  | 3
| 2" Elbow 45* |  | Pcs |  | 4 |  |  | 4
| 2" scoute Coupling |  | Pcs |  | 30 |  |  | 30
2 | Masonry Work
2.1 | 30cm*30cm Anchor and Thurst block on the pipes on transmission main @ every 100m spacing put stone masonary structure of 60cm avarage height at the top hard rock level bedded in cement sand mortar with mix ratio 1:3 |  | No |  | 35 |  |  | 35
| For the Contractor |  |  |  | For the Supervisor
| Name:- Mubarek A. |  |  |  | Name :
| Signature ----------------------------------- |  |  |  | Signature |  | ________________________
| Date -------------------------------------- |  |  |  | Date: |  | ________________________

## Cost Sum...
` |  | BILLS OF QUANTITIES AND SPECIFICATIONS
| FOR | FOR
BORETA WOYO KEBELE WATER SUPPLY AND SANITATION PROJECT
TOTALPRICE SUMMARY
It. No |  | Description | Unit | Qty | Unit Price | Total Cost
A |  | Supply and Installation of Pipes and Fittings | Ls | 1 | 3146700.8 | 3146700.8
B |  | Construction of Water Points with Six Faucet | No. | 6 | 55136.25 | 330817.5
C |  | Construction of Valve Chambers In Net - Work | No. | 6 | 5185.864 | 31115.184
D |  | Construction Of 50mcu Reservoir | No. | 1 | 348639.1 | 348639.1
E |  | Constraction of Valve Chamber for Reservoir | No. | 1 | 6999.25 | 6999.25
F |  | Supply And Installation Of Electro Mechanical Equipment | No. | 1 | 1372130 | 1372130
G |  | Construction of Generator and Guard House In HCB | No. | 1 | 158430 | 158430
H |  | Construction of Anchor Block for Pipe Support | No. | 6 | 3002.2 | 18013.2
I |  | Construction of Trust Block for Pipe Support | No. | 10 | 2556.2 | 25562
J |  | Construction of Road crossing Structure | No. | 1 | 75650 | 75650
K |  | pressure beeak tank | No. | 1 | 18059.1 | 18059.1
|  | Total |  |  |  | 5532116.134
|  | VAT (15%) |  |  |  | 829817.4201
|  | Total including VAT (15%) |  |  |  | 6361933.5541

## BOQ
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
Title: Bill of Quantity and Specification for supply and installation of Pipes and fitting Works
It. No | Description | Unit | Quantity | Unit price | Total Price
A | Supply and installation of Pipes and fitting Works
1 | Earth Works
1.1 | Trench excavation for pipe laying (0.6* 0.8) * 5958 | M3 | 2526.24 | 50 | 126312
1.2 | Trench excavation in hard formation (0.6* 0.8) * 600m | M3 | 288 | 150 | 43200
1.3 | Back fill over the pipe with selected soil type inspected by site Engineer | M3 | 2814.24 | 70 | 196996.8
2 | Supply and laying of different size of GI medium class-B pipes(Techinical sepecification fulfiling IS 1239 (Part) or BS :1387 or equivalent weight and wall thickness
2.1 | 3” | m | 627 | 716 | 448932
2.2 | 2 1/2” | m | 907.5 | 580 | 526350
2.3 | 2” | m | 1721 | 520 | 894920
2.4 | 11/2” | m | 2007.5 | 400 | 803000
3 | Supply and Install different size fittings European standard/Class-B/
3.1 | A) Union
3.1.1 | 3” | No | 7 | 400 | 2800
3.1.2 | 2 1/2” | No | 13 | 300 | 3900
3.1.2 | 2” | No | 16 | 250 | 4000
3.1.3 | 11/2” | No | 22 | 200 | 4400
3.2 | B) Nipples |  |  |  | 0
3.2.1 | 3” | No | 14 | 580 | 8120
3.2.2 | 2 1/2” | No | 26 | 440 | 11440
3.2.3 | 2” | No | 32 | 390 | 12480
3.2.4 | 11/2” | No | 44 | 310 | 13640
3.3 | C) Reducer
3.3.1 | · 3”- 2 1/2'' | No | 1 | 400 | 400
3.3.2 | · 3 ”- 11/2'' | No | 2 | 320 | 640
3.3.3 | · 21/2 ”- 2'' | No | 1 | 260 | 260
3.3.4 | · 2 1/2''-11/2" | No | 3 | 250 | 750
3.3.5 | · 2 ''-11/2" | No | 1 | 200 | 200
3.4 | D) Tee |  |  |  | 0
3.4.0 | 3” | No | 2 | 320 | 640
3.4.1 | 21/2” | No | 3 | 300 | 900
3.4.2 | 2” | No | 2 | 280 | 560
3.4.3 | 11/2” | No | 3 | 200 | 600
3.5 | E) Gate Valve |  |  |  | 0
3.5.1 | 3” Filanged | No | 2 | 5400 | 10800
3.5.2 | 2 1/2” | No | 3 | 350 | 1050
3.5.3 | 2” | No | 1 | 320 | 320
3.5.4 | 1 1/2” | No | 7 | 300 | 2100
3.6 | G)Elbow 90 Degree bends |  |  |  | 0
3.6.1 | 3” | No | 2 | 300 | 600
3.6.2 | 2 1/2” | No | 4 | 280 | 1120
3.6.3 | 2” | No | 2 | 260 | 520
3.6.4 | 1 1/2” | No | 4 | 250 | 1000
4 | Synthetic Paint | Kg | 50 | 250 | 12500
5 | Synthetic Fiber | Kg | 45 | 250 | 11250
| TOTAL |  |  |  | 3146700.8
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
Title:-Bills of Quantities for Construction of Generator and Guard House in HCB
S. No | Description | Unit | Qty | Unit Price | Total Price
H | Construction of Generator and Guard House In HCB
1 | Earth work
1.1 | Site clearing to an averaged depth 0f 20cm to remove top soil and grubbing | m2 | 54 | 20 | 1080
1.2 | Excavation for foundation trench to a depth of notexceeding 100cm below stripped ground level | m3 | 26.8 | 50 | 1340
1.3 | Back filling around a foundation with good dry filling material from the site | m3 | 5.5 | 70 | 385
1.4 | Back filling under a hard core with good and approved selected materials a round the site well rammed and compacted in layers not exceeding 20cm | m3 | 6.7 | 200 | 1340
1.5 | Cart away surplus excavated matrial to a distance of 100m | m3 | 26.8 | 20 | 536
1.6 | Placing 25 cm thick basaltic or equvialent stone hard core well rolled andconsolidated and blinded with crushed stone | m2 | 26.99 | 150 | 4048.5
2 | Masonry work |  |  |  | 0
2.1 | Construction of 50cm thick basaltic or equivalent masonry foundation wall to a depth of 70cm below stripped ground level blended and joined in cementmortar of mix (1:30 | m3 | 13.4 | 1100 | 14740
2.2 | Construction of 50cm thick basaltic or equivalent masonry foundation wall to a height of 35cm above ground level blended and joined in cementmortar of mix (1:3) | m3 | 4.5 | 1100 | 4950
2.3 | Pointing the exposed external wall surface of the foundation wall with cement mortar 1:3 | m2 | 8.8 | 120 | 1056
2.4 | 100cm wide semi - dressed stone pavement around generator house | m2 | 8.8 | 150 | 1320
2.5 | Ponting of stone pavement | m2 | 8.8 | 120 | 1056
2.6 | Construction of semi- circular 30cm diameter drainage ditch as per drawing | ls | 1 | 300 | 300
2.7 | Plastering all exposed surfacs of cloumn, ground and upper tie beam , window and door lintel | m2 | 15.5 | 150 | 2325
3 | Concrete work |  |  |  | 0
3.1 | Placing 50mm thick lean concrete of Grade C-10 with minimum cement content of 150kg/m3 of concrete over the hard core | m3 | 2.1 | 2500 | 5250
3.2 | Casting 15cm thick reinforced concrete for Generator seat (Basement) with Grade C-20 Concrete with minimum cement content of 320kg/m3cost includes supply and installation of Re-bar anda pproved anchor bolts and form work fixing | m3 | 0.98 | 3500 | 3430
3.3 | Placing 15cm thick mass concrete of Grade C-20 with minimum cement content of 320kg/m3 of concrete over the lean concrete | m3 | 5.4 | 2500 | 13500
3.4 | C-20 reinforced concrete for ground tie beam and machine foundation | m3 | 1.47 | 2500 | 3675
3.5 | C-20 reinforced concrete for upper tie beam and lintel | m3 | 1.6 | 2500 | 4000
3.6 | C-20 reinforced concrete for column | m3 | 0.44 | 2500 | 1100
3.7 | Reinforcment bar as per construction drawing | kg | 288 | 55 | 15840
3.8 | Supply, cut, bend and fixing in position sawn wooden form works of equivalent properly erected and strutted with posts and clings having tight joint notto bleed | m2 | 40.4 | 500 | 20200
4 | Wall and roofing |  |  |  | 0
4.1 | Wall work |  |  |  | 0
4.1.1 | 20cm thick hollow concrete block wall | m2 | 46.55 | 350 | 16292.5
4.1.2 | 15cm hollow concrete block wall | m2 | 6.7 | 300 | 2010
4.1.3 | Pointing of internal and external wall surface | m2 | 122 | 150 | 18300
4.2 | Roofing work |  |  |  | 0
4.2.1 | Supply and fix a G-32 G.1 corrugated iron sheets with roof nail having washer fixed to purling of smooth round DN 60mm eucalyptus tree fixed on trusses members made of DN 150mm round eucalyptus tree spaced @ 125cm | m2 | 34.2 | 80 | 2736
4.2.2 | Supply and fix 25*250mm fascial board to purlins | m | 24 | 30 | 720
5 | Doors and windows |  |  |  | 0
5.1 | Supply and fix metal frame door double leaf type with cylinderical lock door size 1.50*2.10m | pcs | 1 | 1500 | 1500
5.2 | Supply and fix metal door size 0.8*2.10m | pcs | 1 | 1200 | 1200
5.3 | Supply and fix metal window size 1.20*1.00m | pcs | 2 | 750 | 1500
5.4 | Supply and fix metal window size 1.00*1.00m | pcs | 1 | 700 | 700
5.5 | Supply and fix mesh wire for insect netting and ventilation as design 75cm high | m2 | 10 | 100 | 1000
6 | Fencing work |  |  |  | 0
6.1 | Fencing around the compound (10*10m) with 10cm well seasond Tid post stand to the height of 2m above ground level with 0.5m deep concrete foundation and bracing diagonals at the corner.The fence shall be constructed with 3mm barbed wire horizontally every 0.2m below 1m and 0.4m above 1m with two way diagonal bracing. | m2 | 100 | 100 | 10000
6.2 | The door shall be corrugated iron sheet 2m*1m including tabular post and pad lock with all accesseries | ls | 1 | 1000 | 1000
| Total sum |  |  |  | 158430
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
Title:- Material requirement and cost estimate of Electromechanical equipments
It. No | Description | Unit | Quantity | Unit Price | total price
G | SUPPLY AND INSTALLATION OF ELECTRO MECHANICAL EQUIPMENT
1 | Supply and Installation of Submersible Pump
1.1 | Supply & Installation of submersible pump-3 with complete set with having
1.2 | Supply & Installation of submersible pump with complete set with having | No | 1 | 500000 | 500000
Q = 1.5l/sec
H = 346m
Pp = 8kw
Efficiency not less than 65%
with its full autotransformer switch board
including the following accessories and specification:-
Cable length =100m
Cable size= 3*25mm2
| Electrode cable length = 160m | m | 160 | 350 | 56000
Electrode cable size=2*1.5mm2 with two electrodes
2 | Supply and Install Diesel Generator |  |  |  |  | 800000
2.1 | Supply and install a compatible generator with complete set and accessories ( accessories include swich board,cable electrode,etc) with having, power of Ps = 16kw & Efficiency not less than 65% | No | 1 | 800000 | 800000
3.2 | Supply and install fittings
3.2.1 | Elbow
| ɸ=3" | pcs | 2 | 400 | 800
3.2.2 | Union
| ɸ=3" | pcs | 1 | 350 | 350
3.2.3 | Water meter flanged
| ɸ=3" | pcs | 2 | 5000 | 10000
3.2.4 | Gate valve
| ɸ=3" | pcs | 2 | 780 | 1560
3.2.5 | Check valve
| ɸ=3" | pcs | 2 | 600 | 1200
3.2.6 | Nipples
| ɸ=3" | pcs | 4 | 180 | 720
3.2.8 | Bolts and nuts | set | 20 | 75 | 1500
| Total sum |  |  |  | 1372130
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
Title: - Bills of Quantities for water point construction with six faucted
It. No. | Description | Unit | Quantity | Unit Price | Total Price | 850 | 5100
B | CONSTRUCTION OF WATER POINTS |  |  |  |  | 535
WITH SIX FAUCETS
1 | Earth work
1.1 | Site clearing to an average depth of 20cm to remove the top vegetated soil | m2 | 25 | 20 | 500
1.2 | Excavation for foundation to a depth of 40 cm | m3 | 6 | 50 | 300
1.3 | Cart away the excavated surplus material to a distance not less than 100m | m3 | 14 | 20 | 280
1.4 | placing 25cm thick hardcore of basaltic or equivalent material well rolled, compacted and blinded with crushed stone | m3 | 4 | 250 | 1000
2 | Masonry work |  |  |  | 0
2.1 | Construction of masonry wall for six faucet water point embedded in 1:3 cement sand mortar mix | m3 | 1.35 | 1100 | 1485
3 | Concrete work |  |  |  | 0
3.1 | Casting 50mm thick lean concrete of 1:3:6 mix ratio(minimum cement content of 150kg/m3) | m3 | 20.06 | 1200 | 24072
3.2 | Mass concrete (1:3:6) mix below foundation wall | m3 | 3 | 2500 | 7500
3.3 | Construction of water point cap with concrete of 1:2:3 mix ratio as per the design drawing | m3 | 0.9 | 2200 | 1980
3.4 | Smooth and well strutted zigba form work | m2 | 19.43 | 75 | 1457.25
4 | Plumbing Works |  |  |  | 0
4.1 | Pipe supply and connecting work |  |  |  | 0
4.1.1 | GS pipe Ø= 11/2" | m | 6 | 400 | 2400
4.1.2 | GS pipe Ø= 1" | m | 6 | 300 | 1800
4.1.3 | GS pipe Ø= 3/4" | m | 3 | 150 | 450
4.2 | Fitting supply and connecting work |  |  |  | 0
4.2.1 | 900 elbow Ø=11/2" | Pcs | 6 | 50 | 300
4.2.2 | Gate valve Ø=11/2" | Pcs | 1 | 80 | 80
4.2.3 | Water meter Ø=11/2" | Pcs | 1 | 1200 | 1200
4.2.4 | Union Ø=11/2" | Pcs | 1 | 50 | 50
4.2.5 | Union Ø=1" | Pcs | 2 | 45 | 90
4.2.6 | Nipples Ø=11/2" | Pcs | 6 | 50 | 300
4.2.7 | Nipples Ø=1" | Pcs | 4 | 45 | 180
4.2.8 | Tee Ø=11/2" | Pcs | 1 | 50 | 50
4.2.9 | Cross tee Ø=1" | Pcs | 2 | 50 | 100
4.2.10 | Reducer Ø= 11/2" - Ø=1" | Pcs | 2 | 50 | 100
4.2.11 | Reducer Ø= 1" - Ø=3/4" | Pcs | 6 | 45 | 270
4.2.12 | Coupling Ø= 3/4" | Pcs | 6 | 25 | 150
3 | Faucet Ø=3/4" | Pcs | 6 | 50 | 300
5 | Micellnious and Finishing works |  |  |  | 0
5.1 | Construction of HCB common walled valve chamber for gate valve and water meter. Price includes supply and fixing anit rust painted and lockable metal valve chamber size 1m*1m with angle iron frame and proper installation of fittings and pointing of HCB | no. | 1 | 1200 | 1200
5.2 | 12mm thick plastering of all exposed surface of concrete and masonry wall with cement mortar mix of 1:3 | m2 | 20 | 75 | 1500
5.3 | 5mm pouring of cement screed placing for floor finish of water points | m2 | 11.28 | 150 | 1692
6 | Fencing work |  |  |  | 0
6.1 | Fencing around the compound (6*6m) with 10cm well seasoned Tid post stand to the height of 2m above ground level with 0.5m deep concrete foundation and bracing diagonals at the corner. The fence shall be constructed with 3mm barbed wire horizontally every 0.1m bellow 1m and 0.2m above 1m with two ways diagonal bracings | m2 | 36 | 100 | 3600
6.2 | Supply and fix corrugated iron sheet door of size 2m*1m with tabular post including pad lock | ls | 1 | 750 | 750
| Total for one water point |  |  |  | 55136.25
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Title:- Material requirement and cost estimate of Pipe and fittings for Road crossing
It. No | Description | Unit | Quantity | Unit Price | Total price
1 | Earth Work
1.1 | excavation for Gravel crossing pipes (0.6* 1.5) * 25m | M3 | 45 | 520 | 23400
1.2 | Back fill over the pipe with selected soil type inspected by site Engineer | M3 | 45 | 50 | 2250
2 | Supply and laying of GI medium class-B pipes for gravel crossing |  |  |  | 0
2.1 | Φ=6'' | m | 50 | 1000 | 50000
| Total cost | Birr |  |  | 75650
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
Title: Bill of Quantities and specification for construction of Anchor blocks & Trust blocks for Pipe Support
It. No | Description | Unit | Qty | Unit Price | Total price
I | Constrution of Anchor Block for Pipe Support
2 | Earth works
1.1 | 2.cm thick site clearing (2m*1.4m) | m3 | 0.56 | 20 | 11.2
1.2 | Foundation excavation depth of 50cm (1.6m*0.1) | m3 | 0.8 | 50 | 40
1.3 | cart away the excavated material | m3 | 0.8 | 20 | 16
1.4 | 20 cm hard core filling | m2 | 0.2 | 150 | 30
1.5 | Filling back the area around the mat foundation after construction | m3 | 0.3 | 200 | 60
2 | concrete work |  |  |  | 0
2.1 | Construct anchor block with 1:2:4 concrete the height of anchor blocks depends on the site condition. | m3 | 0.3 | 2700 | 810
2.2 | reinforcement for concrete |  |  |  | 0
| 10 mm dia at 20 cm c/c for mat foundation | kg | 5 | 58 | 290
| 10mm for column of the Anchor 2 in number | kg | 4 | 58 | 232
| 6mm stirrup | kg | 2 | 58 | 116
| black/tie wire 1.5mm thick | kg | 1.5 | 30 | 45
2.3 | form work |  |  |  | 0
| fix zigba form work to place concrete | m2 | 1.76 | 200 | 352
3 | Galvanized metal clamp with necessary fixtures used to hold pipes on head of anchor blocks | pcs | 1 | 1000 | 1000
| Total cost for one Anchor block |  |  |  | 3002.2 | 15011
10.2 | Construction of masonry thrust block (40cmX40cmx 100cm )
10.2.1 | Earth Work
10.2.1.1 | Clearance top vegetable soil (20cm depth) | m2 | 4 | 20 | 80
10.2.1.2 | Excavation for base foundation (100cm depth) | m3 | 1 | 50 | 50
10.2.1.3 | Cart away surplus excavated material | m3 | 0.16 | 20 | 3.2
10.2.2 | Concrete Work |  |  |  | 0
10.2.2.1 | Mass concrete below Ground level | m3 | 0.5 | 2500 | 1250
10.2.3 | Masonry work |  |  |  | 0
10.2.3.1 | Stone masonry work above ground level | m3 | 0.35 | 1800 | 630
10.2.4 | Pointing of Masonry Block | m2 | 1.6 | 300 | 480
10.2.5 | Plastering the top part of masonary block | m2 | 0.18 | 350 | 63
| Total sum for one Masonry trust block |  |  |  | 2556.2 | 12781
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
TITLE: Bill of Quantities and specification of Valve chambers for Reservoir
S. No | Description | Unit | Qty | Unit Price | Total Price
F | Constraction of Valve Chamber for Reservoir
1.1 | Earth work
1.2 | Site clearing to remove top soil to a depth of 20cm | m3 | 0.8 | 10 | 8
1.3 | Excavation for base foundation | m3 | 2.25 | 28 | 63
1.4 | 25cm thick hardcore filling | m2 | 2.25 | 250 | 562.5
1.5 | Cart away excavated materials | m3 | 2.25 | 15 | 33.75
2 | Masonry Work |  |  |  | 0
2.1 | Stone masonry wall | m3 | 2.25 | 1500 | 3375
3 | Concrete work |  |  |  | 0
3.1 | 10cm thick mass concrete above hardcore | m3 | 0.26 | 1200 | 312
3.2 | 10cm thick RC concrete for roof slab | m3 | 0.51 | 1200 | 612
3.3 | RC bar Ø 10mm | kg | 14 | 58 | 812
3.4 | Black wire Ø 1.5mm | kg | 1 | 30 | 30
4 | Form work |  |  |  | 0
4.1 | Form work for roof slab | m2 | 3.85 | 60 | 231
4.2 | Plastering & other finishing work |  |  |  | 0
4.3 | Plastering internal wall | m2 | 6 | 60 | 360
4.4 | Pointing of external masonry wall | m2 | 8 | 50 | 400
4.5 | Mane hole cover with angle iron frame and sheet metal including pad lock (70cm*70) | ls | 1 | 200 | 200
| Total for one reservoir VC |  |  |  | 6999.25
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
Title: - Bills of Quantities for Valve Chambers Construction In Net - Work
It. No | Description | Unit | Quantity | Unit price | Total Price
C | CONSTRUCTION OF VALVE CHAMBERS IN NET WORK
1 | Earth work
1.1 | Site clearing to remove the top soil to a depth of 20cm | m2 | 4 | 10 | 40
1.2 | Excavation for foundation to a depth of 30cm | m3 | 0.588 | 28 | 16.464
1.3 | Cart away the excavated surplus material for a distance of 100m | m3 | 2 | 15 | 30
1.4 | 25cm thick hard core filling under the floor slab | m3 | 0.49 | 60 | 29.4
2 | Masonry work |  |  |  | 0
2.1 | Construction of 30 cm thick masonry wall embedded with 1:3 mortar | m3 | 1.5 | 1500 | 2250
2.2 | Plastering the internal masonry wall | m2 | 6 | 60 | 360
2.3 | Pointing out the exposed part of the masonry wall | m2 | 8 | 50 | 400
3 | Concrete work |  |  |  | 0
3.1 | Mass concrete for floor slab | m3 | 0.45 | 1200 | 540
3.2 | Supply & Install 700mm*700mm* 3mm thick lockable steel man-hole cover with all fixing hinges & and angle iron frame and all accessories with lockable gate including anti- rust painted | ls | 1 | 750 | 750
4 | Form work |  |  |  | 0
4.1 | Smooth and well strutted zigba form work | m2 | 3.85 | 200 | 770
| Total for one valve chamber |  |  |  | 5185.864
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
Title:- Bill of quantities for Constraction of 50mcu Concrete Sandwiched Masonry Reservoir
I.No | DESCRIPTION | Unit | Qty | Unit Rate | Read out Total Price
1 | Earth work
1.1 | Site clearing to remove the top vegetative part of the soil to a depth of 20cm | m2 | 100 | 20 | 2000
1.2 | Foundation excavation in soft soil to a depth of 75 cm below ground level | m3 | 19.5 | 50 | 975
1.3 | Foundation excavation in rock formation | m3 | 15.2 | 70 | 1064
1.4 | Filling and compacting foundation base with selected sand materials for 20 cms | m3 | 8 | 60 | 480
1.5 | Placing 40 cm thick basaltic stone or equivalent hard core well-rolled consolidated and blinded with gravel | m3 | 28.3 | 550 | 15565
1.6 | Back filling around a foundation with approved selected sand materials from site well rammed in layer of 20 cm | m3 | 8 | 150 | 1200
1.7 | Cart away surplus excavated soil and rock materials from the site to a distance of 100 m | m3 | 29.5 | 20 | 590
2 | Concrete work |  |  |  | 0
2.1 | Casting 100 mm thick Lean concrete over hard-core with Grade C-15 concrete with minimum cement 150kg/m3 mix ration (1:3:6) | m3 | 3.83 | 2200 | 8426
2.2 | Casting 25 cm thick RCC Base slab in Grade C-25 reinforced concrete with minimum cement 360kg/m3 mix 1:11/2:3 | m3 | 10 | 3500 | 35000
2.3 | Casting 20 cm thick RCC Roof cover slab with Grade C-25 reinforced concrete of minimum cement 360kg/m3 mix (1:11/2:3) | m3 | 8.4 | 3500 | 29400
2.4 | Construction of trapezoidal shape section RCC friction key with Grade C-25 reinforced concrete simultaneously with base slab with dimensions a= 15cm, b=25cm, and h=20cm (1:11/2:3) mix | m3 | 1.4 | 3500 | 4900
2.5 | Construction of 10 cm thick reinforced concrete Grade C-25 filled between masonry wall and reinforced with hoop reinforcement of Hexagonal Mesh-Wire of size ¾ tide to diameter 6mm vertical bars @ 30cm c/c | m3 | 8.5 | 2200 | 18700
2.6 | Casting 20cm thick RCC concrete Ring beam of Grade C-25 with minimum cement 360kg/m3 with mix ratio (1:11/2:3) | m3 | 2.58 | 2100 | 5418
2.7 | supply, cut, bend and fix in position reinforcement bars the price shall be include cuting and bending |  |  |  | 0
| ø=6mm | kg | 75 | 58 | 4350
| ø=8mm | kg | 750 | 58 | 43500
| ø=10mm | kg | 1820 | 58 | 105560
| ø=12mm | kg | 160 | 58 | 9280
| Blak wire | kg | 15 | 30 | 450
2.8 | Supply and install 3/4 hexagonal mesh wire for hoop stress and wall tied to ɸ6mm vertical bars @30cm c/c | m2 | 51 | 8 | 408
2.9 | Fixing of good quality wooden or metal form work firmly with strong strutting/scaffolding & tight to avoid Bleeding & Bulging out | m2 | 4 | 150 | 600
3 | Masonry work |  |  |  | 0
3.1 | Construction of 2 x 20 cm thick masonry Wall on both side of the concrete - Core embedded with cement Sand mortar of mix 1 : 3 | m3 | 24 | 750 | 18000
3.2 | Chiseling and floor finish 45 mm thick trawl and smooth finish with 1:3 cement Sand mortar screed | m2 | 25 | 50 | 1250
3.3 | Semi dressed stone pavement around the reservoir 1.0 m wide cemented with in 1:3 mix cement mortar | m2 | 28 | 150 | 4200
3.4 | Construction of semi-circular 30 cm diameter drainage ditch as per drawing | m | 44 | 40 | 1760
4 | Plastering and other finishing work |  |  |  | 0
4.1 | Chiseling and 12mm plastering the whole inner wall face and exposed face of all concrete works with 3coats of cement sand mortar of 1:3 mix | m2 | 53 | 75 | 3975
4.2 | Pointing the whole External face of the masonry wall with cement mortar mix 1 : 2 | m2 | 90 | 65 | 5850
4.3 | 5cm cement screed for floor finish | m2 | 150 | 30 | 4500
4.4 | Supply and placed tarred paper between lean concrete and floor slab | m2 | 30.18 | 20 | 603.6
4.5 | Supply and painting the lean concrete with bituminous mastic | m2 | 30.18 | 25 | 754.5
5 | Supply and Install Class-B Pipes and Fittings |  |  |  | 0
5.1 | Pipes |  |  |  | 0
5.1.1 | Supply and install ɸ=2 1/2" GI pipe for inlet | m | 6 | 140 | 840
5.1.2 | Supply and install ɸ=3" GI pipe for outlet | m | 6 | 140 | 840
5.1.3 | Supply and install ɸ=21/2" GI pipe for overflow | m | 6 | 140 | 840
5.1.4 | Supply and install ɸ=21/2" GI pipe for drainage | m | 6 | 140 | 840
5.1.5 | Supply and install pipe=21/2" vent pipe with Dom shape | m | 3 | 140 | 420
5.2 | Fittings |  |  |  | 0
5.2.1 | ɸ=2 1/2" Elbow 90 degree | pcs | 4 | 120 | 480
5.2.2 | ɸ=3" Elbow 90 degree | pcs | 2 | 120 | 240
5.2.3 | ɸ=2" Union | pcs | 2 | 175 | 350
5.2.4 | ɸ=21/2" Union | pcs | 2 | 180 | 360
5.2.5 | ɸ=2" Nipples | pcs | 8 | 40 | 320
5.2.6 | ɸ=21/2" Nipples | pcs | 4 | 75 | 300
5.2.7 | ɸ=21/2" Gate valve | pcs | 2 | 210 | 420
5.2.8 | ɸ= 3" Gate valve | pcs | 1 | 400 | 400
5.2.9 | ɸ=3" Flanged water meter | pcs | 1 | 3200 | 3200
5.2.10 | ɸ=21/2" Tee | pcs | 2 | 180 | 360
5.2.11 | ɸ=3" Tee | pcs | 1 | 250 | 250
5.2.12 | Nuts and bolts | no. | 24 | 20 | 480
6 | Micllonouse work |  |  |  | 0
6.1 | Supply & Install lockable steel man-hole cover with all fixing hinges & accessories with lock gate (Design) | no. | 1 | 800 | 800
6.2 | Supply and install both external & internal ladder made of class B, G S pipe of DN 25 mm length 3.0 m having extra 1.0 m high handle at the top for external ladder | no. | 2 | 1850 | 3700
6.3 | Fencing around the compound (8*8m) with 10cm well seasoned Tid post stand to the height of 2m above ground level with 0.5m deep concrete foundation and bracing diagonals at the corner. The fence shall be constructed with 3mm barbed wire horizontally every 0.1m bellow 1m and 0.2m above 1m with two ways diagonal bracings | m2 | 64 | 60 | 3840
6.4 | Supply and fix corrugated iron sheet door of size2m*1m with tabular post including pad lock | ls | 1 | 400 | 400
7 | Cleaning and Disinfecting | ls | 1 | 200 | 200
| Total for one 50mcu Masonry Reservior |  |  |  | 348639.1
Project: - Boreta Woyo Kebele Water Supply and Sanitation Project
Location: - Sidama Zone, Bona zuriya Woreda
Title:- Bill of Quantities for Break Pressure Tank
I.No | DESCRIPTION | Unit | Quantity | Unit price | Amount
1 | Earth Work
1.1 | Site Clearing of depth of 20cm | M3 | 1.3 | 20 | 26
1.2 | Excavation of foundation 20cm | m3 | 1.6 | 80 | 128
1.3 | Cart away surplus excavated material | m3 | 3.39 | 20 | 67.8
1.4 | 20cm thick basaltic hard core | m3 | 5.29 | 90 | 476.1
2 | Masonry Work |  |  |  | 0
2.1 | Stone masonry wall as per drawing | m3 | 5.52 | 1100 | 6072
2.2 | Pointing of external masonry wall | M2 | 6.72 | 120 | 806.4
3 | Concrete work |  |  |  | 0
3.1 | 10cm thick lean concrete above the hard core | m3 | 0.61 | 2200 | 1342
3.2 | 45mm thick cement screening of floor | m3 | 0.25 | 2000 | 500
3.3 | Plastering of internal wall | m2 | 0.16 | 130 | 20.8
3.4 | Pointing of external wall | m2 | 1.2 | 120 | 144
4 | Supply and install 1mm sheet metal for man hole (60cm*60cm) | No | 1 | 1200 | 1200
5 | Supply and install GI pipes and fitting (Class B) |  |  |  | 0
| Ф 2’’ for outlet , Drainage and overflow | m | 6 | 270 | 1620
| Float valve Ф 2’’ | pcs | 1 | 800 | 800
| Gate Valve Ф 2’’ | pcs | 2 | 1500 | 3000
| Union Ф 2’’ | pcs | 2 | 300 | 600
| Nipples Ф 2’’ | pcs | 2 | 120 | 240
| Reinforcement bar Ф 10mm with tie bare | kg | 17 | 58 | 986
| Black wire 1.5mm | kg | 1 | 30 | 30
| Total for1(One) break pressure tank | Birr |  |  | 18059.1

## Population
Table 1.2 Population projection and water demand analysis in Boreta woyo village
Description | Growth rate per year(%) | Year
|  | 2010 | 2011 | 2016 | 2021 | 2026 | 2031
Population projection | 3 | 3654 | 3763.62 | 4363.0671 | 5057.9906 | 5863.5973 | 6797.5164
Average per capital demand(l/c/d) |  |  | 25 | 25 | 25 | 25 | 25
Average daily water demand(l/d) |  |  | 94090.5 | 109076.6773 | 126449.7641 | 146589.9332 | 169937.9091
Maximum day demand(l/s) |  |  | 1.3068 | 1.515 | 1.7562 | 2.036 | 2.3602
Peak hourly demand(l/s) |  |  | 2.3523 | 2.7269 | 3.1612 | 3.6647 | 4.2484
Reservior capacity(m^3) |  |  | 31.3635 | 36.3589 | 42.1499 | 48.8633 | 56.646
Adopted reservior capacity(m^3) |  |  | 50 | 50 | 50 | 50 | 50 | <25 | <50 | <75 | <100 | <125 | <150
[8 empty] | 25 | 50 | 75 | 100 | 125 | 150

## Distribution
Altitiude of 50m3 Reservior site above mean sea level= 2341m+3 | [16 empty] | Inches | mm
IN.pt | St.pt | Pipe L.th | P.Dia (mm) | V.cy (m/s) | D.g (l/sec) | H. loss (m) | Cum. HL | rh | Cum. rH | Free Head | Node Elv. | Location |  |  |  |  | 1.5 | 38.1 | 38
R | X | 150 | 75 | 1.1115 | 4.908 | 2.5188 | 2.5188 | -29 | -29 | 26.4812 | 2312 |  | 4" |  |  |  | 2 | 50.8 | 51
X | X1 | 100 | 75 | 1.1115 | 4.908 | 1.6792 | 4.1979 | -3 | -32 | 27.8021 | 2309 |  | 3" | 570 | 57 | 627 | 2.5 | 63.5 | 63
X1 | WP1 | 30 | 38 | 0.72163 | 0.818 | 0.41908 | 4.617 | -6 | -38 | 33.383 | 2303 | Sintaro sire | 21/2" | 825 | 82.5 | 907.5 | 3 | 76.2 | 75
X1 | X2 | 150 | 75 | 0.92626 | 4.09 | 1.7491 | 5.9471 | -18 | -50 | 44.0529 | 2291 |  | 2" | 330 | 33 | 363 | 3.5 | 88.9 | 89
X2 | X3 | 170 | 75 | 0.92648 | 4.091 | 1.9833 | 7.9304 | -30 | -80 | 72.0696 | 2261 |  | 11/2" | 1825 | 182.5 | 2007.5 | 4 | 101.6 | 100
X3 | P | 200 | 38 | 0.72181 | 0.8182 | 2.7953 | 10.7256 | -28 | -108 | 97.2744 | 2233 |  |  |  |  | 3905
P | P1 | 250 | 38 | 0.72181 | 0.8182 | 3.4941 | 14.2197 | 21 | -87 | 72.7803 | 2254 |  |  |  | 355
P1 | wp2 | 200 | 38 | 0.72181 | 0.8182 | 2.7953 | 17.015 | -7 | -94 | 76.985 | 2247 | Gobena siraro | L(Total) | 3550 | 355 |  |  |  | 100
X3 | X4 | 200 | 63 | 1.0502 | 3.272 | 3.569 | 3.569 | -26 | -26 | 22.431 | 2235 | p break |  | 3905 | 3905 |  |  |  | 150
X4 | X5 | 90 | 63 | 1.0502 | 3.272 | 1.606 | 5.175 | -18 | -44 | 38.825 | 2217 |  |  | 3905
X5 | X6 | 280 | 63 | 1.0502 | 3.272 | 4.9966 | 10.1716 | -21 | -65 | 54.8284 | 2196
X6 | X7 | 120 | 63 | 1.0502 | 3.272 | 2.1414 | 12.313 | -28 | -93 | 80.687 | 2168
X7 | X8 | 135 | 63 | 1.0502 | 3.272 | 2.4091 | 14.7221 | 11 | -82 | 67.2779 | 2179
X8 | St.pt | 60 | 38 | 0.72181 | 0.8182 | 0.83858 | 15.5607 | -2 | -84 | 68.4393 | 2177 | School tap
X8 | X9 | 175 | 50 | 1.2503 | 2.4538 | 5.5777 | 20.2998 | -6 | -88 | 67.7002 | 2173
X9 | X10 | 80 | 50 | 1.2508 | 2.4546 | 2.5515 | 22.8513 | -4 | -92 | 69.1487 | 2169
X10 | H.tp | 40 | 38 | 0.72181 | 0.8182 | 0.55905 | 23.4104 | 18 | -74 | 50.5896 | 2187 | Health tap
X10 | X11 | 75 | 50 | 0.83383 | 1.6364 | 1.0631 | 23.9144 | 8 | -84 | 60.0856 | 2177
X11 | wp3 | 60 | 38 | 0.72181 | 0.8182 | 0.83858 | 24.753 | 7 | -77 | 52.247 | 2184 | Germa Nare
X11 | X12 | 430 | 38 | 0.72181 | 0.8182 | 6.0098 | 29.9242 | -26 | -110 | 80.0758 | 2151
X12 | X13 | 440 | 38 | 0.72181 | 0.8182 | 6.1496 | 36.0738 | 7 | -103 | 66.9262 | 2158
X13 | X14 | 85 | 38 | 0.72181 | 0.8182 | 1.188 | 37.2618 | -17 | -120 | 82.7382 | 2141
X14 | wp4 | 30 | 38 | 0.72181 | 0.8182 | 0.41929 | 37.6811 | 6 | -114 | 76.3189 | 2147 | Asefaw Butuna
| L | 3550

## P&G
Pump capacity and Power Requirement The work done by Pump and Generator Is Calculated as follows.
S.NO | TDH CALCULATION STEPES | DIMENSION | unit
1 | pumping distance | 1358.5 | M
2 | Discharge | 1.5 | L/S
3 | ALLOWANCE | 15 | M
4 | Pump position /Rizing main/ | 145 | M
5 | DELIVERY HEAD(Elevation difference) | 167 | M
6 | RESERVOIR HEIGHT | 3 | M
7 | HL (IN DELEVERY PIPE ) | 14.7093 | M
8 | VELOCITY IN DELEVERY PIPE | 0.76433 | M/S
9 | DIAMETER OF DELEVERY PIPE | 50 | mm
10 | DISCHARGE | 1.5 | L/S
11 | MINOR HL | 0.73546 | M
12 | TDH | 345.4447 | M
13 | TDH take | 346 | m
POWER OF SUBMESIBLE PUMP CALCULATION
1 | TDH | 346 | M
2 | Discharge | 1.5 | L/S
3 | efficiency of pump(E) | 60 | %
4 | POWER OF PUMP=TDH*Q | 7.8281 | Kw
102*E
| Pp take | 8 | Kw
|  | 10 | Kva
power supply (power of generator)=pg
1 | power of pump(Pp) | 8 | kw
2 | Pg = *1.85*Pp | 14.8 | KW
3 | Pg take | 16 | KW
4 | Pg take | 20 | KVA

## Pressur
Pressure main pipe line to existing 300m3 Reserviour | [11 empty] | Inches | mm
IN.pt | St.pt | Pipe Length | Pipe Dia (mm) | Velocity (m/s) | Discharge (l/sec) | Head loss(m) | Cum. HL | rH | Cum. rH | Node Elv. | Remark | 1.5 | 38.1 | 38
BH | B | 150 | 50 | 0.76433 | 1.5 | 1.7866 | 1.7866 | 10 | 10 | 2184 | New Line | 2 | 50.8 | 51
B | B1 | 155 | 50 | 0.76433 | 1.5 | 1.8461 | 3.6327 | 28 | 38 | 2212 |  | 2.5 | 63.5 | 63
B1 | B2 | 130 | 50 | 0.76433 | 1.5 | 1.5483 | 5.181 | 14 | 52 | 2226 |  | 3 | 76.2 | 75
B2 | B3 | 120 | 50 | 0.76433 | 1.5 | 1.4292 | 6.6102 | 15 | 67 | 2241 |  | 3.5 | 88.9 | 89
B3 | B4 | 215 | 50 | 0.76433 | 1.5 | 2.5607 | 9.171 | 38 | 105 | 2279
B4 | B5 | 240 | 50 | 0.76433 | 1.5 | 2.8585 | 12.0294 | 32 | 137 | 2311
B5 | R | 225 | 50 | 0.76433 | 1.5 | 2.6798 | 14.7093 | 30 | 167 | 2341 |  | 4 | 101.6 | 100
|  | 1358.5 | 1358
1235
123.5
Note on I4: Adane-PC: P1-P0(B.H)

## Layout
BORETA WOYO WSP LAYOUT
Gobena siraro
Sintaro sire
Germa Nare
Asefaw Butuna
50M3
wp2
wp1
Health tap
School Water p.
wp3
wp4
2.5"=907m
1.5"=60m
2"=280m
2"=83m
1 .5"=40m
1.5"=50m
1.5"=1150m
1.5"=715m
3"=275m
3"=352m
1.5"=30m

## Concatenate
Prssure Line from BH to Reservior
Length | Easting | Northing | Elivation | Remark
0 | 473400 | 726848 | 2174 | BH | 473400,726848
148.5295 | 473306 | 726963 | 2184 | J1 | 473306,726963 | 150
153.0555 | 473205 | 727078 | 2212 | J2 | 473205,727078 | 155
128.0156 | 473143 | 727190 | 2226 | J3 | 473143,727190 | 130
114.8651 | 473068 | 727277 | 2241 | J4 | 473068,727277 | 120
208.6648 | 472898 | 727398 | 2279 | J5 | 472898,727398 | 215
234.6487 | 472704 | 727530 | 2311 | J6 | 472704,727530 | 240
223.2219 | 472486 | 727482 | 2341 | R | 472486,727482 | 225
DISTRIBUTION OF NEW PIPE LINE FROM 50M3 R
Length | Easting | Northing | Elivation | Remark
0 | 472486 | 727482 | 2341 | R |  | 472486,727482
152.0691 | 472637 | 727500 | 2312 | X |  | 472637,727500
85 | 472721 | 727513 | 2309 | X1 |  | 472721,727513
81.3019 | 472718 | 727493 | 2303 | Wp1 | Sintaro sire | 472718,727493
0 | 472721 | 727513 | 2309 | X1 |  | 472721,727513
148.1891 | 472847 | 727435 | 2291 | X2 |  | 472847,727435
169.2926 | 472979 | 727329 | 2261 | X3 |  | 472979,727329
197.6082 | 473174 | 727361 | 2233 | P |  | 473174,727361
248.4774 | 473209 | 727607 | 2254 | P1 |  | 473209,727607
195.8622 | 473308 | 727776 | 2247 | Wp2 | Gobena siraro | 473308,727776
0 | 472979 | 727329 | 2261 | X3 |  | 472979,727329
186.4537 | 473137 | 727230 | 2235 | X4 | p break | 473137,727230
82.4621 | 473157 | 727150 | 2217 | X5 |  | 473157,727150
267.8246 | 473334 | 726949 | 2196 | X6 |  | 473334,726949
119.708 | 473395 | 726846 | 2168 | X7 |  | 473395,726846
80.3057 | 473402 | 726766 | 2179 | X8 |  | 473402,726766
55.8032 | 473435 | 726721 | 2176 | School tap |  | 473435,726721
0 | 473402 | 726766 | 2179 | X8 |  | 473402,726766
222.441 | 473416 | 726544 | 2173 | X9 |  | 473416,726544
72.6911 | 473426 | 726472 | 2169 | X10 |  | 473426,726472
38.2884 | 473401 | 726443 | 2187 | Health tap |  | 473401,726443
0 | 473426 | 726472 | 2169 | X10 |  | 473426,726472
74.7329 | 473442 | 726399 | 2177 | X11 |  | 473442,726399
46.669 | 473475 | 726366 | 2184 | Wp3 | Germa Nare | 473475,726366
0 | 473442 | 726399 | 2177 | X11 |  | 473442,726399
424.1556 | 473280 | 726007 | 2151 | X12 |  | 473280,726007
425.18 | 473363 | 725590 | 2158 | X13 |  | 473363,725590
20.3961 | 473359 | 725570 | 2147 | Wp4 | Asefaw Butuna | 473359,725570

## Sheet2
Altitiude of 50m3 Reservior site above mean sea level= 2341m+3 | [16 empty] | Inches | mm
IN.pt | St.pt | Pipe L.th | P.Dia (mm) | V.cy (m/s) | D.g (l/sec) | H. loss (m) | Cum. HL | rh | Cum. rH | Free Head | Node Elv. | Location |  |  |  |  | 1.5 | 38.1 | 38
R | X | 150 | 75 | 1.2968 | 5.726 | 3.4283 | 3.4283 | -29 | -29 | 25.5717 | 2312 |  | 4" |  |  |  | 2 | 50.8 | 51
X | X1 | 100 | 75 | 1.2968 | 5.726 | 2.2855 | 5.7138 | -3 | -32 | 26.2862 | 2309 |  | 3" | 570 | 57 | 627 | 2.5 | 63.5 | 63
X1 | WP1 | 30 | 38 | 0.72163 | 0.818 | 0.41908 | 6.1329 | -6 | -38 | 31.8671 | 2303 | Sintaro sire | 21/2" | 1080 | 108 | 1188 | 3 | 76.2 | 75
X1 | X2 | 150 | 75 | 1.1115 | 4.908 | 2.5188 | 8.2326 | -18 | -50 | 41.7674 | 2291 |  | 2" | 75 | 7.5 | 82.5 | 3.5 | 88.9 | 89
X2 | X3 | 170 | 75 | 1.1118 | 4.9092 | 2.856 | 11.0886 | -30 | -80 | 68.9114 | 2261 |  | 11/2" | 2457 | 245.7 | 2702.7 | 4 | 101.6 | 100
X3 | P | 200 | 38 | 0.72181 | 0.8182 | 2.7953 | 13.8838 | -28 | -108 | 94.1162 | 2233 |  |  |  |  | 4600.2
P | P1 | 250 | 38 | 0.72181 | 0.8182 | 3.4941 | 17.3779 | 21 | -87 | 69.6221 | 2254 |  |  |  | 418.2
P1 | wp2 | 200 | 38 | 0.72181 | 0.8182 | 2.7953 | 20.1732 | -7 | -94 | 73.8268 | 2247 | Gobena siraro | L(Total) | 4182 | 418.2 |  | 4.5 | 114.3 | 100
X3 | X4 | 200 | 63 | 1.3127 | 4.09 | 5.5765 | 5.5765 | -26 | -26 | 20.4235 | 2235 | need break p |  | 4600.2 | 4600.2 |  | 6 | 152.4 | 150
X4 | X5 | 90 | 63 | 1.3127 | 4.09 | 2.5094 | 8.086 | -18 | -44 | 35.914 | 2217 |  |  | 4600 |  |  | 6.5 | 165.1
X5 | X6 | 280 | 63 | 1.3127 | 4.09 | 7.8072 | 15.8932 | -21 | -65 | 49.1068 | 2196 |  | 5958 | 5958 |  |  | 8 | 203.2
X6 | Y | 350 | 38 | 0.72181 | 0.8182 | 4.8917 | 20.7849 | -44 | -109 | 88.2151 | 2152
Y | Y1 | 62 | 38 | 0.72181 | 0.8182 | 0.86653 | 21.6514 | -2 | -111 | 89.3486 | 2150
Y1 | Y2 | 130 | 38 | 0.72163 | 0.818 | 1.816 | 23.4674 | -11 | -122 | 98.5326 | 2139
Y2 | wp3 | 110 | 38 | 0.72181 | 0.8182 | 1.5374 | 25.0048 | 29 | -93 | 67.9952 | 2168 | Awoke Hameso
X6 | X7 | 120 | 63 | 1.0502 | 3.272 | 2.1414 | 18.0346 | -28 | -93 | 74.9654 | 2168
X7 | X8 | 135 | 63 | 1.0502 | 3.272 | 2.4091 | 20.4436 | 11 | -82 | 61.5564 | 2179
X8 | St.pt | 30 | 38 | 0.72181 | 0.8182 | 0.41929 | 20.8629 | -2 | -84 | 63.1371 | 2177 | School tap
X8 | X9 | 175 | 63 | 0.78757 | 2.4538 | 1.7563 | 22.2 | -6 | -88 | 65.8 | 2173
X9 | X10 | 80 | 63 | 0.78783 | 2.4546 | 0.80342 | 23.0034 | -4 | -92 | 68.9966 | 2169
X10 | H.tp | 50 | 38 | 0.72181 | 0.8182 | 0.69882 | 23.7022 | 18 | -74 | 50.2978 | 2187 | Health tap
X10 | X11 | 75 | 50 | 0.83383 | 1.6364 | 1.0631 | 24.0665 | 8 | -84 | 59.9335 | 2177
X11 | wp4 | 60 | 38 | 0.72181 | 0.8182 | 0.83858 | 24.9051 | 7 | -77 | 52.0949 | 2184 | Germa Nare
X11 | X12 | 430 | 38 | 0.72181 | 0.8182 | 6.0098 | 30.0763 | -26 | -110 | 79.9237 | 2151
X12 | X13 | 440 | 38 | 0.72181 | 0.8182 | 6.1496 | 36.2259 | 7 | -103 | 66.7741 | 2158
X13 | X14 | 85 | 38 | 0.72181 | 0.8182 | 1.188 | 37.4139 | -17 | -120 | 82.5861 | 2141
X14 | wp5 | 30 | 38 | 0.72181 | 0.8182 | 0.41929 | 37.8332 | 6 | -114 | 76.1668 | 2147 | Asefaw Butuna
| L | 4182